| COUNTY OF FRESNO |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Request for QUOTATION |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | NUMBER: 990-5161 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| May 29, 2013 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ORG/Requisition: 7205/ 9701300029 |  |  |  |  |  |  | PURCHASING USE |  |  |  | /tmp/in/input.doc |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | fef |  |  |  |  |  |  |  |  |  |  |  |
| IMPORTANT: SUBMIT QUOTATION IN SEALED PACKAGE WITH QUOTATION NUMBER, CLOSING DATE AND BUYER’S NAME MARKED CLEARLY ON THE OUTSIDE TO: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| COUNTY OF FRESNO, Purchasing 4525 EAST HAMILTON AVENUE, 2nd Floor FRESNO, CA 93702-4599 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Closing date of bid will be at 2:00 p.m., on June 27, 2013. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| QUOTATIONS WILL BE CONSIDERED LATE WHEN THE OFFICIAL PURCHASING TIME CLOCK READS 2:00 P.M. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Quotations will be opened and publicly read at that time. All quotation information will be available for review after contract award. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Clarification of specifications is to be directed to: Craig Nickel, e-mail CountyPurchasing@co.fresno.ca.us, phone (559) 600-7115, FAX (559) 600-7126. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| GENERAL CONDITIONS: See “County Of Fresno Purchasing Standard Instructions And Conditions For Request For Proposals (RFP’S) and Requests for Quotations (RFQ’S)” attached. Check County of Fresno Purchasing’s Open Solicitations website at http://www2.co.fresno.ca.us/0440/Bidshome2.asp for RFQ/RFP documents and changes. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| BIDDER TO COMPLETE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| UNDERSIGNED AGREES TO FURNISH THE COMMODITY OR SERVICE STIPULATED IN THE ATTACHED QUOTATION SCHEDULE AT THE PRICES AND TERMS STATED, SUBJECT TO THE “COUNTY OF FRESNO PURCHASING STANDARD INSTRUCTIONS AND CONDITIONS FOR REQUEST FOR QUOTATIONS (RFP’S) AND REQUESTS FOR QUOTATIONS (RFQ’S)”ATTACHED. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Except as noted on individual items, the following will apply to all items in the Quotation Schedule. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Complete delivery will be made within |  |  |  |  |  |  |  | calendar days after receipt of Order. |  |  |  |  |  |  |  |  |  |  |
| - A cash discount of |  |  |  |  | % |  |  |  |  | days will apply. |  |  |  |  |  |  |  |  |
| Company |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Address |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| City |  |  |  |  |  |  |  |  |  |  |  |  | State |  | Zip Code |  |  |  |
| ( ) |  |  |  | ( ) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Telephone Number |  |  |  | Facsimile Number |  |  |  |  |  |  |  |  | E-mail Address |  |  |  |  |  |
| Signed By |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Print Name |  |  |  |  |  |  |  |  | Title |  |  |  |  |  |  |  |  |  |

COUNTY OF FRESNO PURCHASING

STANDARD INSTRUCTIONS AND CONDITIONS FOR
REQUESTS FOR PROPOSALS (RFP'S) AND REQUESTS FOR QUOTATIONS (RFQ'S)

Note: the reference to “bids” in the following paragraphs applies to RFP's and RFQ's

## GENERAL CONDITIONS

By submitting a bid the bidder agrees to the following conditions.  These conditions will apply to all subsequent purchases based on this bid.

- BID PREPARATION:

  - All prices and notations must be typed or written in ink.  No erasures permitted.  Errors may be crossed out, initialed and corrections printed in ink by person signing bid.

  - Brand Names: Brand names and numbers when given are for reference.  Equal items will be considered, provided the offer clearly describes the article and how it differs from that specified.  In the absence of such information it shall be understood the offering is exactly as specified.

  - State brand or make of each item.  If bidding on other than specified, state make, model and brand being bid and attach supporting literature/specifications to the bid.

  - Bid on each item separately.  Prices should be stated in units specified herein.  All applicable charges must be quoted; charges on invoice not quoted herein will be disallowed.

  - Time of delivery is a part of the consideration and must be stated in definite terms and must be adhered to.  F.O.B.  Point shall be destination or freight charges must be stated.

  - All bids must be dated and signed with the firm’s name and by an authorized officer or employee.

  - Unless otherwise noted, prices shall be firm for one hundred eighty (180) days after closing date of bid.

- SUBMITTING BIDS:

  - Each bid must be submitted on forms provided in a sealed envelope/package with bid number and closing date and time on the outside of the envelope/package.

  - Interpretation: Should any discrepancies or omissions be found in the bid specifications or doubt as to their meaning, the bidder shall notify the Buyer in writing at once.  The County shall not be held responsible for verbal interpretations.  Questions regarding the bid must be received by Purchasing at least five (5) working days before bid opening.  All addenda issued shall be in writing, duly issued by Purchasing and incorporated into the contract.

  - ISSUING AGENT/AUTHORIZED CONTACT: This RFP/RFQ has been issued by County of Fresno, Purchasing.  Purchasing shall be the vendor’s sole point of contact with regard to the RFP/RFQ, its content, and all issues concerning it.

All communication regarding this RFP/RFQ shall be directed to an authorized representative of County Purchasing.  The specific buyer managing this RFP/RFQ is identified on the cover page, along with his or her telephone number, and he or she should be the primary point of contact for discussions or information pertaining to the RFP/RFQ.  Contact with any other County representative, including elected officials, for the purpose of discussing this RFP/RFQ, its content, or any other issue concerning it, is prohibited unless authorized by Purchasing.  Violation of this clause, by the vendor having unauthorized contact (verbally or in writing) with such other County representatives, may constitute grounds for rejection by Purchasing of the vendor’s quotation.

The above stated restriction on vendor contact with County representatives shall apply until the County has awarded a purchase order or contract to a vendor or vendors, except as follows.  First, in the event that a vendor initiates a formal protest against the RFP/RFQ, such vendor may contact the appropriate individual, or individuals who are managing that protest as outlined in the County’s established protest procedures.  All such contact must be in accordance with the sequence set forth under the protest procedures.  Second, in the event a public hearing is scheduled before the Board of Supervisors to hear testimony prior to its approval of a purchase order or contract, any vendor may address the Board.

  - Bids received after the closing time will NOT be considered.

  - Bidders are to bid what is specified or requested first.  If unable to or unwilling to, bidder may bid alternative or option, indicating all advantages, disadvantages and their associated cost.

  - Public Contract Code Section 7028.15

Where the State of California requires a Contractor’s license, it is a misdemeanor for any person to submit a bid unless specifically exempted.

- FAILURE TO BID:

  - If not bidding, return bid sheet and state reason for no bid or your name may be removed from mailing list.

- TAXES, CHARGES AND EXTRAS:

  - County of Fresno is subject to California sales and/or use tax (8.225%).  Please indicate as a separate line item if applicable.

  - DO NOT include Federal Excise Tax.  County is exempt under Registration No.  94-73-03401-K.

  - County is exempt from Federal Transportation Tax.  Exemption certificate is not required where shipping papers show consignee as County of Fresno.

  - Charges for transportation, containers, packing, etc.  will not be paid unless specified in bid.

- W-9 – REQUEST FOR TAXPAYER IDENTIFICATION NUMBER AND CERTIFICATION & CALIFORNIA FORM 590 WITHHOLDING EXEMPTION CERTIFICATE:

Upon award of bid, the vendor shall submit to County Purchasing, a completed IRS Form W-9 - Request for Taxpayer Identification Number and Certification and a California Form 590 Withholding Exemption Certificate if not currently a County of Fresno approved vendor.

- AWARDS:

  - Award(s) will be made to the most responsive responsible bidder; however, the Fresno County Local Vendor Preference and/or the Disabled Veteran Business Enterprise Preference shall take precedence when applicable.  Said Preferences apply only to Request for Quotations for materials, equipment, and/or supplies only (no services); the preference do not apply to Request for Proposals.  RFQ evaluations will include such things as life-cycle cost, availability, delivery costs and whose product and/or service is deemed to be in the best interest of the County.  The County shall be the sole judge in making such determination.

  - Unless bidder gives notice of all-or-none award in bid, County may accept any item, group of items or on the basis of total bid.

  - The County reserves the right to reject any and all bids and to waive informalities or irregularities in bids.

  - Award Notices are tentative: Acceptance of an offer made in response to this RFP/RFQ shall occur only upon execution of an agreement by both parties or issuance of a valid written Purchase Order by Fresno County Purchasing.

  - After award, all bids shall be open to public inspection.  The County assumes no responsibility for the confidentiality of information offered in a bid.

- TIE BIDS:

All other factors being equal, the contract shall be awarded to the Fresno County vendor or, if neither or both are Fresno County vendors, it may be awarded by the flip of a coin in the presence of witnesses or the entire bid may be rejected and re-bid.  If the General Requirements of the RFQ state that they are applicable, the provisions of the Fresno County Local Vendor Preference shall take priority over this paragraph.

- PATENT INDEMNITY:

The vendor shall hold the County, its officers, agents and employees, harmless from liability of any nature or kind, including costs and expenses, for infringement or use of any copyrighted or uncopyrighted composition, secret process, patented or unpatented invention, article or appliance furnished or used in connection with this bid.

- SAMPLES:

Samples, when required, must be furnished and delivered free and, if not destroyed by tests, will upon written request (within thirty (30) days of bid closing date) be returned at the bidder's expense.  In the absence of such notification, County shall have the right to dispose of the samples in whatever manner it deems appropriate.

- RIGHTS AND REMEDIES OF COUNTY FOR DEFAULT:

  - In case of default by vendor, the County may procure the articles or service from another source and may recover the cost difference and related expenses occasioned thereby from any unpaid balance due the vendor or by proceeding against performance bond of the vendor, if any, or by suit against the vendor.  The prices paid by the County shall be considered the prevailing market price at the time such purchase is made.

  - Articles or services, which upon delivery inspection do not meet specifications, will be rejected and the vendor will be considered in default.  Vendor shall reimburse County for expenses related to delivery of non-specified goods or services.

  - Regardless of F.O.B.  point, vendor agrees to bear all risks of loss, injury or destruction to goods and materials ordered herein which occur prior to delivery and such loss, injury or destruction shall not release vendor from any obligation hereunder.

- DISCOUNTS:

Terms of less than fifteen (15) days for cash payment will be considered as net in evaluating this bid.  A discount for payment within fifteen (15) days or more will be considered in determining the award of bid.  Discount period will commence either the later of delivery or receipt of invoice by the County.  Standard terms are Net forty-five (45) days.

- SPECIAL CONDITIONS IN BID SCHEDULE SUPERSEDE GENERAL CONDITIONS:

The “General Conditions” provisions of this RFP/RFQ shall be superseded if in conflict with any other section of this bid, to the extent of any such conflict.

- SPECIAL REQUIREMENT:

With the invoice or within twenty-five (25) days of delivery, the seller must provide to the County a Material Safety Data Sheet for each product, which contains any substance on “The List of 800 Hazardous Substances”, published by the State Director of Industrial Relations.  (See Hazardous Substances Information and Training Act.  California State Labor Code Sections 6360 through 6399.7.)

- RECYCLED PRODUCTS/MATERIALS:

Vendors are encouraged to provide and quote (with documentation) recycled or recyclable products/materials which meet stated specifications.

- YEAR COMPLIANCE WARRANTY:

Vendor warrants that any product furnished pursuant to this Agreement/order shall support a four-digit year format and be able to accurately process date and time data from, into and between the twentieth and twenty-first centuries, as well as leap year calculations.  "Product" shall include, without limitation, any piece or component of equipment, hardware, firmware, middleware, custom or commercial software, or internal components or subroutines therein.  This warranty shall survive termination or expiration of this Agreement.

In the event of any decrease in product functionality or accuracy related to time and/or date data related codes and/or internal subroutines that impede the product from operating correctly using dates beyond December 31, 1999, vendor shall restore or repair the product to the same level of functionality as warranted herein, so as to minimize interruption to County's ongoing business process, time being of the essence.  In the event that such warranty compliance requires the acquisition of additional programs, the expense for any such associated or additional acquisitions, which may be required, including, without limitation, data conversion tools, shall be borne exclusively by vendor.  Nothing in this warranty shall be construed to limit any rights or remedies the County may otherwise have under this Agreement with respect to defects other than year performance.

- PARTICIPATION:

Bidder may agree to extend the terms of the resulting contract to other political subdivision, municipalities, and tax-supported agencies.

Such participating Governmental bodies shall make purchases in their own name, make payment directly to bidder, and be liable directly to the bidder, holding the County of Fresno harmless.

- CONFIDENTIALITY:

All services performed by vendor shall be in strict conformance with all applicable Federal, State of California and/or local laws and regulations relating to confidentiality, including but not limited to, California Civil Code, California Welfare and Institutions Code, Health and Safety Code, California Code of Regulations, Code of Federal Regulations.

Vendor shall submit to County’s monitoring of said compliance.

Vendor may be a business associate of County, as that term is defined in the “Privacy Rule” enacted by the Health Insurance Portability and Accountability Act of 1996 (HIPAA).  As a HIPAA Business Associate, vendor may use or disclose protected health information (“PHI”) to perform functions, activities or services for or on behalf of County as specified by the County, provided that such use or disclosure shall not violate HIPAA and its implementing regulations.  The uses and disclosures if PHI may not be more expansive than those applicable to County, as the “Covered Entity” under HIPAA’s Privacy Rule, except as authorized for management, administrative or legal responsibilities of the Business Associate.

Vendor shall not use or further disclose PHI other than as permitted or required by the County, or as required by law without written notice to the County.

Vendor shall ensure that any agent, including any subcontractor, to which vendor provides PHI received from, or created or received by the vendor on behalf of County, shall comply with the same restrictions and conditions with respect to such information.

- APPEALS:

Appeals must be submitted in writing within seven (7) working days after notification of proposed recommendations for award.  A “Notice of Award” is not an indication of County’s acceptance of an offer made in response to this RFP/RFQ.  Appeals should be submitted to County of Fresno Purchasing, 4525 E.  Hamilton Avenue, Fresno, California 93702-4599.  Appeals should address only areas regarding RFP contradictions, procurement errors, quotation rating discrepancies, legality of procurement context, conflict of interest, and inappropriate or unfair competitive procurement grievance regarding the RFP/RFQ process.

Purchasing will provide a written response to the complainant within seven (7) working days unless the complainant is notified more time is required.

If the protesting bidder is not satisfied with the decision of Purchasing, he/she shall have the right to appeal to the Purchasing Agent/CAO within seven (7) business days after Purchasing’s notification; except if, notified to appeal directly to the Board of Supervisors at the scheduled date and time.

If the protesting bidder is not satisfied with Purchasing Agent/CAO’s decision, the final appeal is with the Board of Supervisors.

- OBLIGATIONS OF CONTRACTOR:

  - CONTRACTOR shall perform as required by the ensuing contract.  CONTRACTOR also warrants on behalf of itself and all subcontractors engaged for the performance of the ensuing contract that only persons authorized to work in the United States pursuant to the Immigration Reform and Control Act of 1986 and other applicable laws shall be employed in the performance of the work hereunder.

  - CONTRACTOR shall obey all Federal, State, local and special district laws, ordinances and regulations.

- AUDITS & RETENTION:

The Contractor shall maintain in good and legible condition all books, documents, papers, data files and other records related to its performance under this contract.  Such records shall be complete and available to Fresno County, the State of California, the federal government or their duly authorized representatives for the purpose of audit, examination, or copying during the term of the contract and for a period of at least three (3) years following the County's final payment under the contract or until conclusion of any pending matter (e.g., litigation or audit), whichever is later.  Such records must be retained in the manner described above until all pending matters are closed.

- DISCLOSURE – CRIMINAL HISTORY & CIVIL ACTIONS:

Applies to Request for Proposal (RFP); does not apply to Request for Quotation (RFQ) unless specifically stated elsewhere in the RFQ document.

In their proposal, the bidder is required to disclose if any of the following conditions apply to them, their owners, officers, corporate managers and partners (hereinafter collectively referred to as “Bidder”):

- Within the three-year period preceding the proposal, they have been convicted of, or had a civil judgment rendered against them for:

  - fraud or a criminal offense in connection with obtaining, attempting to obtain, or performing a public (federal, state, or local) transaction or contract under a public transaction;

  - violation of a federal or state antitrust statute;

  - embezzlement, theft, forgery, bribery, falsification, or destruction of records; or

  - false statements or receipt of stolen property

Within a three-year period preceding their proposal, they have had a public transaction (federal, state, or local) terminated for cause or default.

- DATA SECURITY:

Individuals and/or agencies that enter into a contractual relationship with the COUNTY for the purpose of providing services must employ adequate controls and data security measures, both internally and externally to ensure and protect the confidential information and/or data provided to contractor by the COUNTY, preventing the potential loss, misappropriation or inadvertent access, viewing, use or disclosure of COUNTY data including sensitive or personal client information; abuse of COUNTY resources; and/or disruption to COUNTY operations.

Individuals and/or agencies may not connect to or use COUNTY networks/systems via personally owned mobile, wireless or handheld devices unless authorized by COUNTY for telecommuting purposes and provide a secure connection; up to date virus protection and mobile devices must have the remote wipe feature enabled.  Computers or computer peripherals including mobile storage devices may not be used (COUNTY or Contractor device) or brought in for use into the COUNTY’s system(s) without prior authorization from COUNTY’s Chief Information Officer and/or designee(s).

No storage of COUNTY’s private, confidential or sensitive data on any hard-disk drive, portable storage device or remote storage installation unless encrypted according to advance encryption standards (AES of 128 bit or higher).

The COUNTY will immediately be notified of any violations, breaches or potential breaches of security related to COUNTY’s confidential information, data and/or data processing equipment which stores or processes COUNTY data, internally or externally.

COUNTY shall provide oversight to Contractor’s response to all incidents arising from a possible breach of security related to COUNTY’s confidential client information.  Contractor will be responsible to issue any notification to affected individuals as required by law or as deemed necessary by COUNTY in its sole discretion.  Contractor will be responsible for all costs incurred as a result of providing the required notification.

- PURCHASING LOCATION & HOURS:

Fresno County Purchasing is located at 4525 E.  Hamilton Avenue (second floor), Fresno, CA 93702.  Non-holiday hours of operation are Monday through Friday, 8:00 A.M.  to 12:00 Noon and 1:00 P.M.  to 5:00 P.M.  PST; Purchasing is closed daily from 12:00 Noon to 1:00 P.M.  The following holiday office closure schedule is observed:

| January 1* |  | New Year's Day |
| --- | --- | --- |
| Third Monday in January |  | Martin Luther King, Jr.’s Birthday |
| Third Monday in February |  | Washington - Lincoln Day |
| March 31* |  | Cesar Chavez’ Birthday |
| Last Monday in May |  | Memorial Day |
| July 4* |  | Independence Day |
| First Monday in September |  | Labor Day |
| November 11* |  | Veteran's Day |
| Fourth Thursday in November |  | Thanksgiving Day |
| Friday following Thanksgiving |  |  |
| December 25* |  | Christmas |
| * When this date falls on a Saturday, the holiday is observed the preceding Friday. If the date falls on a Sunday, the holiday is observed the following Monday. |  |  |

BIDDING INSTRUCTIONS
CONTRACT SERVICE AND SUPPLY

The County of Fresno is soliciting bids to provide all labor, materials, equipment, etc., to perform maintenance, repair, inspection, and monitoring for the County’s fire and intrusion alarm systems.  The County of Fresno has approximately ninety-one (91) facilities with intrusion alarm systems, sixty (60) facilities with fire alarm systems, and thirty-eight (38) facilities that require monitoring services located throughout the County of Fresno.  The intent of this RFQ is to identify vendor(s) that are interested in performing contracted maintenance and repair services as well as quarterly and annual inspections for fire alarm systems, annual inspections for intrusion alarm systems, testing of each of those systems and monitoring of those facilities identified in the RFQ.  The County of Fresno’s delivery of service to the citizens and employees of the County is dependent upon the reliable operation of the identified systems.

This RFQ is divided into four (4) separate sections; Notifier alarm systems, general fire alarm systems, intrusion alarm systems, and monitoring.  Vendors will not have to bid on all four sections of this RFQ; to be considered for the award of a contract in one specific section.

NOTE: County reserves the right to award each service type separately.  The bidder must state if his/her proposal for one service type is contingent upon award of one or more other service types as defined under the Scope of Work.

AWARD:  Award will be made to the vendor(s) offering the equipment and system deemed to be to the best advantage of the County.  The County shall be the sole judge in making such determination.  Award Notices are tentative: Acceptance of an offer made in response to this RFQ shall occur only upon execution of an agreement by both parties or issuance of a valid written Purchase Order by Fresno County Purchasing.

COPIES:  Submit one (1) original and two (2) copies of your quotation no later than the RFQ closing date and time as stated on the front of this document, to County of Fresno Purchasing.

ISSUING AGENT: This RFQ has been issued by County of Fresno, Purchasing.  The Purchasing shall be the vendor’s sole point of contact with regard to the RFQ, its content, and all issues concerning it.

AUTHORIZED CONTACT: All communication regarding this RFQ shall be directed to an authorized representative of County Purchasing.  The specific buyer managing this RFQ is identified on the cover page, along with his or her telephone number, and he or she should be the primary point of contact for discussions or information pertaining to the RFQ.  Contact with any other County representative, including elected officials, for the purpose of discussing this RFQ, it content, or any other issue concerning it, is prohibited unless authorized by Purchasing.  Violation of this clause, by the vendor having unauthorized contact (verbally or in writing) with such other County representatives, may constitute grounds for rejection by Purchasing of the vendor’s quotation.

The above stated restriction on vendor contact with County representatives shall apply until the County has awarded a purchase order or contract to a vendor or vendors, except as follows.  First, in the event that a vendor initiates a formal protest against the RFQ, such vendor may contact the appropriate individual, or individuals who are managing that protest as outlined in the County’s established protest procedures.  All such contact must be in accordance with the sequence set forth under the protest procedures.  Second, in the event a public hearing is scheduled before the Board of Supervisors to hear testimony prior to its approval of a purchase order or contract, any vendor may address the Board.

VENDOR CONFERENCE: On June 12, 2013 at 10:00 a.m., a vendor's conference will be held in which the scope of the project and quotation requirements will be explained.  The meeting will be held at the office of County of Fresno Purchasing, 4525 E.  Hamilton (between Cedar and Maple), 2nd Floor, Fresno, California, 93702.  Minutes will be prepared and distributed to all bidders only if necessary to clarify substantive items raised during the bidders' conference.

Bidders are to contact Craig Nickel at County of Fresno Purchasing, (559) 600-7115, if they are planning to attend the conference.

INTERPRETATION OF RFQ: Vendors must make careful examination of the requirements, specifications and conditions expressed in the RFQ and fully inform themselves as to the quality and character of services required.  If any person planning to submit a proposal finds discrepancies in or omissions from the RFQ or has any doubt as to the true meaning or interpretation, correction thereof may be requested at the scheduled Vendor Conference (see above).  Any change in the RFQ will be made only by written addendum, duly issued by the County.  The County will not be responsible for any other explanations or interpretations.

Questions may be submitted subsequent to the Vendor Conference, subject to the following conditions:

- Such questions are submitted in writing to the County Purchasing at least 10 County business days prior to the Request for Quotation closing date.  Questions must be directed to the attention of the buyer identified on page one.

- Such questions are submitted with the understanding that County can respond only to questions it considers material in nature.

- Questions shall be delivered to County of Fresno Purchasing, 4525 E.  Hamilton Avenue, Fresno, CA 93702 or faxed to (559) 600-7126.  If faxing the bidder must confirm receipt by phone ((559) 600-7110) within one-half (1/2) hour of transmission.

NOTE: The bidder is encouraged to submit all questions at the Vendor Conference.  Time limitations can prevent a response to questions submitted after the conference.

PAYMENT:  County will make partial payments for all purchases made under this contract/purchase order and accumulated during the month.

RIGHT TO REJECT BIDS:  The County reserves the right to reject any and all bids and to waive informalities or irregularities in bids.

TERM:  The initial contract period shall be three (3) years.

RENEWAL:  Agreement shall automatically renew for an additional one (1) year period except when written notice is delivered by either party to the other expressing intent not to renew.  Such notice must be delivered a minimum of sixty (60) days prior to the next expiration date of this Agreement.  The maximum number of automatic one (1) year renewal periods under this Agreement is two (2).

RENEWAL:  Agreement may be renewed for two (2) additional one (1) year periods by the mutual written consent of all parties.

QUANTITIES:  Quantities shown in the bid schedule are approximate and the County guarantees no minimum amount.  The County reserves the right to increase or decrease quantities.

SPECIFICATIONS AND EQUALS:  Brand names, where used, are a means of establishing quality and style.  Bidders are invited to quote their equals.  Alternate offers are to be supported by literature, which fully describes items that you are bidding.

No exceptions to or deviations from this specification will be considered unless each exception or deviation is specifically stated by the bidder, in the designated places.  If no exceptions or deviations are shown, the bidder will be required to furnish items exactly as specified herein.  The burden of proof of compliance with this specification is the responsibility of the bidder.

LITERATURE:  Bidders shall submit literature, which fully describes items on which they are bidding, not later than the closing date of this bid.  Any and all literature submitted must be stamped with bidders name and address.

MERCHANDISE RETURNABLE FOR FULL CREDIT:  Bidder agrees to accept for full credit any merchandise sold by him on contract or award resulting from this bid, if returned in good condition by the County.

GUARANTEE AGAINST DEFECTS:  All items are to carry a full guarantee against defects in materials and workmanship and guarantee against breakage and other malfunctions when performing work for which they are designed.

ORDERING:  Orders will be placed as required by the various County Departments.

INVOICING:  All invoices are to be delivered in duplicate to ISD Security, 2220 Tulare St.; Plaza level Fresno Ca.  93721.  Reference shall be made to the purchase order/contract number and equipment number if applicable on the invoice.

SAMPLES:  On request, samples of the products on which you are bidding shall be made available to the County.  County will designate where samples are to be delivered.

Successful bidder's samples may be retained for checking against delivery, in which case allowance will be made to vendor.

RENEWAL:  Contract may be renewed for an additional year by mutual written consent.

VENDOR ASSISTANCE:  Successful bidder shall furnish, at no cost to the County, a representative to assist County departments in determining their product requirements.

TERMINATION:  This agreement may be terminated by the County at any time upon written notice.

HOLD HARMLESS CLAUSE:  Contractor agrees to indemnify, save, hold harmless and at County's request, defend the County, its officers, agents and employees, from any and all costs and expenses, damages, liabilities, claims and losses occurring or resulting to County in connection with the performance, or failure to perform, by Contractor, its officers, agents or employees under this Agreement and from any and all costs and expenses, damages, liabilities, claims and losses occurring or resulting to any person, firm or corporation who may be injured or damaged by the performance, or failure to perform, of Contractor, its officers, agents or employees under this Agreement.

ASSURANCES:  Any contract awarded under this RFQ must be carried out in full compliance with The Civil Rights Act of 1964, The Americans With Disabilities Act of 1990, their subsequent amendments, and any and all other laws protecting the rights of individuals and agencies.  The County of Fresno has a zero tolerance for discrimination, implied or expressed, and wants to ensure that policy continues under this RFQ.  The contractor must also guarantee that services, or workmanship, provided will be performed in compliance with all applicable local, state, or federal laws and regulations pertinent to the types of services, or project, of the nature required under this RFQ.  In addition, the contractor may be required to provide evidence substantiating that their employees have the necessary skills and training to perform the required services or work.

INDEPENDENT CONTRACTOR:  In performance of the work, duties and obligations assumed by Bidder under this agreement, it is mutually understood and agreed that Bidder, including any and all of Bidder's officers, agents, and employees will at all times be acting and performing as an independent contractor, and shall act in an independent capacity and not as an officer, agent, servant, employee, joint venturer, partner, or associate of the County.  Furthermore, County shall have no right to control or supervise or direct the manner or method by which Bidder shall perform its work and function.  However, County shall retain the right to administer this agreement so as to verify that Bidder is performing its obligations in accordance with the terms and conditions thereof.  Bidder and County shall comply with all applicable provisions of law and the rules and regulations, if any, of Governmental authorities having jurisdiction over matters the subject thereof.

Because of its status as an independent contractor, Bidder waives any and all employment rights and benefits available to County employees.  Bidder shall be solely liable and responsible for providing to, or on behalf of, its employees all legally required employee benefits.  In addition, Bidder shall be solely responsible and save County harmless from all matters relating to payment of Contractor's employees, including compliance with Social Security, withholding, and all other regulations governing such matters.  It is acknowledged that during the term of this agreement, Bidder may be providing services to others unrelated to the County or to this agreement.

PRICES:  Bidder agrees that prices quoted are maximum for the contract period, and in the event of a price decline such lower prices shall be extended to the County of Fresno.

MATERIALS TO BE NEW:  All materials shall be new and of merchantable grade, free from defect.  No bid will be considered unless it is accompanied by a complete list of manufacturer's catalog numbers of the items, which the bidder proposes to furnish, together with full descriptive literature on all items so enumerated.  If item proposed differs from these specifications, bidder shall present specific explanation of functioning and structural characteristics for those details which differ from the specifications listed herein.

EXAMINATION OF SITE:  Where work is to be performed on County site, each bidder shall have examined the site of work before bidding and shall be responsible for having acquired full knowledge of the job and of all problems affecting it.  No variations or allowance from the contract sum will be made because of lack of such examination.

DAMAGE TO EXISTING WORK:  Damage to existing construction, equipment, planting, etc., by the contractor in the performance of his work shall be replaced or repaired and restored to original condition by the contractor.

CLEAN-UP:  The Contractor shall at all times, keep the premises clean from accumulation of waste materials or rubbish caused by his employees or work and shall remove all resulting work debris from the job site.

SUPERVISION:  The Contractor shall give efficient supervision to the work, using therein the skill and diligence for which he is remunerated in the contract price.  He shall carefully inspect the site and study and compare all drawings, specifications and other instructions, as ignorance of any phase of any of the features or conditions affecting the contract will not excuse him from carrying out its provisions to its full intent.

STANDARD OF PERFORMANCE:  All work shall be performed in a good and workmanlike manner.

SAFEGUARDS:  The contractor shall provide safeguards, in conformity with all local codes and ordinances as may be required.

BONDS

Bid Deposit (Security):  Each bidder shall provide and submit with their bid, a bid deposit in an amount equal to ten percent (10%) of the total bid amount.

In the event a bidder or bidders fail to enter into an agreement(s) for the services offered under their bid(s), such bid deposit shall be forfeited to County.

The bid deposit shall be in the form of a cashier’s check, irrevocable letter of credit or a bid bond.  The bidder’s security when in the form of a cashier’s check or bond shall be made payable to the County of Fresno.

The bid deposit of the apparent successful bidder(s) shall be retained by County until the agreement(s) have been fully executed by the apparent successful bidder(s) and the County or until County determines that all bids have been rejected.

All other bid deposits (except bonds) will be returned promptly following execution of all agreements or when all bids have been rejected.  Bonds will be returned only upon written request from the bidder.

INSURANCE:

Without limiting the COUNTY's right to obtain indemnification from CONTRACTOR or any third parties, CONTRACTOR, at its sole expense, shall maintain in full force and effect, the following insurance policies or a program of self-insurance, including but not limited to, an insurance pooling arrangement or Joint Powers Agreement (JPA) throughout the term of the Agreement:

- Commercial General Liability

Commercial General Liability Insurance with limits of not less than One Million Dollars ($1,000,000) per occurrence and an annual aggregate of Two Million Dollars ($2,000,000).  This policy shall be issued on a per occurrence basis.   COUNTY may require specific coverages including completed operations, products liability, contractual liability, Explosion-Collapse-Underground, fire legal liability or any other liability insurance deemed necessary because of the nature of this contract.

- Automobile Liability

Comprehensive Automobile Liability Insurance with limits for bodily injury of not less than Two Hundred Fifty Thousand Dollars ($250,000.00) per person, Five Hundred Thousand Dollars ($500,000.00) per accident and for property damages of not less than Fifty Thousand Dollars ($50,000.00), or such coverage with a combined single limit of Five Hundred Thousand Dollars ($500,000.00).  Coverage should include owned and non-owned vehicles used in connection with this Agreement.

- Professional Liability

If CONTRACTOR employs licensed professional staff, (e.g., Ph.D., R.N., L.C.S.W., M.F.C.C.) in providing services, Professional Liability Insurance with limits of not less than One Million Dollars ($1,000,000.00) per occurrence, Three Million Dollars ($3,000,000.00) annual aggregate.

- Worker's Compensation

A policy of Worker's Compensation insurance as may be required by the California Labor Code.

Contractor shall obtain endorsements to the Commercial General Liability insurance naming the County of Fresno, its officers, agents, and employees, individually and collectively, as additional insured, but only insofar as the operations under this Agreement are concerned.  Such coverage for additional insured shall apply as primary insurance and any other insurance, or self-insurance, maintained by County, its officers, agents and employees shall be excess only and not contributing with insurance provided under contractor's policies herein.  This insurance shall not be cancelled or changed without a minimum of thirty (30) days advance written notice given to County.

Within thirty (30) days from the date contractor executes this Agreement, CONTRACTOR shall provide certificates of insurance and endorsement as stated above for all of the foregoing policies, as required herein, to the County of Fresno, Jerry Morris, Chief of Security, ISD Security, 2220 Tulare St.  Plaza Level, Fresno Ca.  93721, stating that such insurance coverage have been obtained and are in full force; that the County of Fresno, its officers, agents and employees will not be responsible for any premiums on the policies; that such Commercial General Liability insurance names the County of Fresno, its officers, agents and employees, individually and collectively, as additional insured, but only insofar as the operations under this Agreement are concerned; that such coverage for additional insured shall apply as primary insurance and any other insurance, or self-insurance, maintained by County, its officers, agents and employees, shall be excess only and not contributing with insurance provided under contractor's policies herein; and that this insurance shall not be cancelled or changed without a minimum of thirty (30) days advance, written notice given to County.

In the event contractor fails to keep in effect at all times insurance coverage as herein provided, the County may, in addition to other remedies it may have, suspend or terminate this Agreement upon the occurrence of such event.

All policies shall be with admitted insurers licensed to do business in the State of California.  Insurance purchased shall be purchased from companies possessing a current A.M.  Best, Inc.  rating of A FSC VII or better.

| Name of Insurance Carrier: |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Public Liability: |  |  |  | Expires: |  |
| Worker's Compensation: |  |  |  | Expires: |  |

Proof of maintenance of adequate insurance will be required before award is made to vendor.

GUARANTEE: The bidder shall state his written guarantee here:

REFERENCES:  Provide a list of three (3) client references that are presently using services being quoted (Name, phone number and contact person.)

GUARANTEED PICK-UP AND/OR DELIVERY:  Bidder will be considered in award of bid only if they can guarantee.  Enter guarantee on this line (i.e.  number of days from receipt of order to delivery):

| By: | (Authorized Signature) |
| --- | --- |

WARRANTY AND SERVICE LOCATION:

- BIDDER TO COMPLETE:

State the warranty and/or guarantee provisions applicable to this equipment or attach warranty form with your bid.

State specific location where service and/or maintenance can be obtained.  Failure to furnish this information will be cause for rejection of bid.

The County may require additional items from those in bid schedule.

Price list for additional items:

| A |  | percent discount from manufacturer's enclosed price list will be allowed on |
| --- | --- | --- |
| purchases of all additional items. |  |  |

State name of price list, indicate applicable price column and give effective date of price list here:

Prices on additional items will be based on successful bidder's firm discount prices from manufacturer's enclosed published price list.

State Purchase Order mailing address:

SELF-DEALING TRANSACTION DISCLOSURE (financial)

Is the bidder a for-profit or non-profit corporation?

|  | No, the bidder is not a for-profit or non-profit corporation. If you check this box, you do not need to fill out the Self-Dealing Transaction Disclosure Form, please have the authorized representative sign and date the form at the bottom of the page. |
| --- | --- |
|  | Yes, the bidder is a for-profit or non-profit corporation. If you check this box, you must fill out the Self-Dealing Transaction Disclosure Form, sign and date it. |

Bidders shall complete a SELF-DEALING TRANSACTION DISCLOSURE FORM, provided herein, for each applicable corporate director of the bidding company.  The signed form(s) shall be submitted as a part of the company’s proposal or quotation.

Complete the form and indicate “NONE” under part 3 when your company is a corporation and no directors are involved with a Self-Dealing Transaction.  The form must be signed by an individual authorized to legally bind the corporation when no directors have a Self-Dealing Transaction.

DISCLOSURE OF SELF-DEALING TRANSACTIONS: The following provision will be incorporated into ensuing agreements.  It shall apply only when the CONTRACTOR is operating as a corporation (a for-profit or non-profit corporation) or if during the term of the agreement, CONTRACTOR changes its status to operate as a corporation.

This provision is only applicable if the CONTRACTOR is operating as a corporation (a for-profit or non-profit corporation) or if during the term of this agreement, the CONTRACTOR changes its status to operate as a corporation.

Members of the CONTRACTOR’s Board of Directors shall disclose any self-dealing transactions that they are a party to while CONTRACTOR is providing goods or performing services under this agreement.  A self-dealing transaction shall mean a transaction to which the CONTRACTOR is a party and in which one or more of its directors has a material financial interest.  Members of the Board of Directors shall disclose any self-dealing transactions that they are a party to by completing and signing a Self-Dealing Transaction Disclosure Form (Exhibit #) and submitting it to the COUNTY prior to commencing with the self-dealing transaction or immediately thereafter.

SELF-DEALING TRANSACTION DISCLOSURE FORM instructions

In order to conduct business with the County of Fresno (hereinafter referred to as “County”), members of a contractor’s board of directors (hereinafter referred to as “County Contractor”), must disclose any self-dealing transactions that they are a party to while providing goods, performing services, or both for the County.  A self-dealing transaction is defined below:

“A self-dealing transaction means a transaction to which the corporation is a party and which one or more of its directors has a material financial interest”

The definition above will be utilized for purposes of completing the disclosure form.

- Enter board member’s name, job title (if applicable), and date this disclosure is being made.

- Enter the board member’s company/agency name and address.

- Describe in detail the nature of the self-dealing transaction that is being disclosed to the County.  At a minimum, include a description of the following:

  - The name of the agency/company with which the corporation has the transaction; and

  - The nature of the material financial interest in the Corporation’s transaction that the board member has.

- Describe in detail why the self-dealing transaction is appropriate based on applicable provisions of the Corporations Codes.

- Form must be signed by the board member that is involved in the self-dealing transaction described in Sections (3) and (4).

Form provided on following page.

SELF-DEALING TRANSACTION DISCLOSURE FORM

| - Company Board Member Information: |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Name: |  |  |  | Date: |  |
| Job Title: |  |  |  |  |  |
| - Company/Agency Name and Address: |  |  |  |  |  |
| - Disclosure (Please describe the nature of the self-dealing transaction you are a party to) |  |  |  |  |  |
| - Explain why this self-dealing transaction is consistent with the requirements of Corporations Code 5233 (a) |  |  |  |  |  |
| - Authorized Signature |  |  |  |  |  |
| Signature: |  |  | Date: |  |  |

COUNTY OF FRESNO

LOCAL VENDOR BID PREFERENCE
AND
DISABLED VETERAN BUSINESS ENTERPRISE BID PREFERENCE

The Local Vendor and Disabled Veteran Business Enterprise Preferences apply to this RFQ.

Whenever the Purchasing Agent purchases supplies, materials and/or equipment for the County through the use of competitive bids, the Purchasing Agent, in evaluating the price or bid for such supplies, materials and/or equipment shall determine if each bidder is a Fresno County Local Vendor (FCLV) and/or a Disabled Veteran Business Enterprise (DVBE).  Bidders that are either an FCLV or a California State Certified DVBE may be granted a preference when determining the award of a bid.  FCLV and DVBE, for the purposes of this section, are defined below.

- Fresno County Local Vendor (FCLV)

  - The vendor has its headquarters, distribution point or locally-owned franchise located in or having a street address within the County for at least six (6) months immediately prior to the issuance of the request for competitive bids by the Purchasing Agent; and

  - The vendor holds any required business license by a jurisdiction located in Fresno County; and

  - The vendor employs at least one (1) full-time or two (2) part-time employees whose primary residence is located within Fresno County, or if the business has no employees, shall be at least fifty percent (50%) owned by one or more persons whose primary residence(s) is located within Fresno County.

- Disabled Veteran Business Enterprise (DVBE)

A vendor must be certified by the State of California as a Disabled Veteran Business Enterprise (DVBE) as of the close of the competitive bid process in which they are participating.  State certification as a DVBE is issued by the California Department of Internal Services.

Other Conditions

- Any vendor claiming to be a FCLV as defined above, or a DVBE shall so certify in writing to the Purchasing Agent.  The Purchasing Agent shall not be required to verify the accuracy of any such certifications, and shall have sole discretion to determine if a vendor meets the definition of a FCLV.

- Any person or business falsely claiming to be a FCLV or DVBE under this section shall be ineligible to transact any business with the County for a period of not less than three (3) months and not more twenty-four (24) months as determined at the sole discretion of the Purchasing Agent.  The Purchasing Agent shall also have the right to terminate all or any part of any contract entered into with such person or business.

- In the event that the Purchasing Agent rejects a vendor’s claim that they are a FCLV and/or a DVBE, and as such declares them to be ineligible, such vendor shall be entitled to a public hearing before the Board of Supervisors and a five (5) day notice of the time and place thereof.

- This section shall not apply to contracts required by state or federal statutes or regulations to be awarded to the lowest responsible bidder or otherwise exempted from local preference.

Preferences

FCLVs and DVBEs that submit a bid within five percent (5%) of the lowest responsive and responsible bid will, under certain specified circumstances, qualify to submit a new bid within two County business days of County’s notification.  Such new bids must be in an amount less than or equal to the lowest responsive and responsible bid previously determined by the Purchasing Agent.  If the Purchasing Agent receives new bids from qualifying FCLVs and/or DVBEs, he shall award the contract to the FCLV or DVBE that submits the lowest responsive and responsible bid.  If no new bids are received, the contract shall be awarded to the original low bidder as announced by the Purchasing Agent.  The lowest responsive and responsible bid shall be solely determined by the Purchasing Agent.

The Purchasing Agent will consider the following four categories of bidder relative to the Fresno County Local Vendor Preference and the Disabled Veteran Business Enterprise Preference.

Vendor Preference Categories

- FCLV – Fresno County Local Vendor as defined above.

- DVBE – Disabled Veteran Business Enterprise as defined above; a DVBE is not also a FCLV unless specifically designated as such.

- FCLV & DVBE – A vendor that is both a Fresno County Local Vendor and Disabled Veteran Business Enterprise as defined above.

- VNP – Vendor No Preference; A vendor that is neither a Fresno County Local Vendor nor a Disabled Veteran Business Enterprise.

The following table identifies the various combinations of vendor preference categories that could be received in response to an RFQ.  It also indicates when a vendor qualifies for a re-bid under either the FCLV or DVBE Preference.

The first column of the table identifies the Vendor Preference Category of the bidder that the Purchasing Agent has determined to be the lowest cost, responsive and responsible bidder.  Each vendor preference category is shown in the columns to the right.  The table indicates when a vendor category qualifies for a re-bid relative to the low bid category in the first column (read left to right).

| Low Bid Submitted by Vendor Preference Category | FCLV & DVBE | FCLV | DVBE (Not a FCLV) | VNP |
| --- | --- | --- | --- | --- |
| FCLV & DVBE Award to Low Bid No Re-bid Opportunity | No Re-bid Opportunity | No Re-bid Opportunity | No Re-bid Opportunity | No Re-bid Opportunity |
| VNP Award Subject to Preference Re-bid | May Re-bid when within 5% of low bid | May Re-bid when within 5% of low bid | May Re-bid when within 5% of low bid | No Re-bid Opportunity |
| FCLV Award Subject to Preference Re-bid | May Re-bid when within 5% of low bid | No Re-bid Opportunity | No Re-bid Opportunity | No Re-bid Opportunity |
| DVBE (Not a FCLV) Award Subject to Preference Re-bid | May Re-bid when within 5% of low bid | May Re-bid when within 5% of low bid | No Re-bid Opportunity | No Re-bid Opportunity |

Applying the Preferences

In determining the award of a Request for Quotation (RFQ), the Purchasing Agent will first identify the lowest cost responsive and responsible bidder, and award will be made to that vendor when such vendor is both a FCLV and a DVBE.

If the lowest such bidder is not an FCLV, it will be determined if the Local Vendor Preference and/or the DVBE Preference are applicable to other bidders.  The preferences will then apply to bids submitted by FCLVs and DVBEs that are within 5% of the designated low bid.  The vendors submitting bids that are within the 5% will be granted an opportunity to submit a new bid.  It must be stressed that in the event of a tie between a FCLV and a DVBE that is not a FCLV; the FCLV shall take precedence in award of the contract.  This condition is necessary to remain consistent with Fresno County Charter Section 12 (h), which specifically calls for a preference to local vendors.

When the lowest responsive and responsible bidder is a FCLV, other bidders who are both FCLVs and DVBEs will have the opportunity to re-bid.

When the lowest responsive and responsible bid is from a non-local DVBE, all FCLVs will be offered a re-bid opportunity.

PREFERENCE CERTIFICATION
Local VendOR 
AND/OR
DISABLED VETERANS BUSINESS ENTERPRISE

The Fresno County Local Vendor Preference (FCLV) and the Disabled Veteran Business Enterprise Preference (DVBE) are applicable to this Request for Quotation as previously explained.

Qualified Vendors that desire consideration as a FCLV and/or a DVBE under this RFQ must complete the “Statement of Local Vendor Certification” and/or the “Statement of DVBE Certification”; each is included below, and submit it/them as a part of their quotation.  Late submittals of these certification forms will not be considered.  Submission of either or both certifications will qualify the vendor for treatment as a local vendor or a DVBE for purposes of this RFQ only.  The certification(s) made under this RFQ do not qualify the vendor for a preference under any other RFQ.

NOTIFICATION OF RE-BID

If a vendor’s bid qualifies under the Fresno County Local Vendor Preference or the DVBE Preference, the vendor will be notified of his/her opportunity to re-bid.  If so notified, the Vendor must submit his/her re-bid within two County business days of notification.

Notification will be issued by e-mail or Fax, whichever is preferred by the vendor.  Notification to Vendor shall be considered complete upon County’s transmission of e-mail or Fax.  It will be the vendor’s responsibility to check his/her e-mail or Fax messages for notification.  The vendor’s delay in retrieval of his/her notification will not alter the two (2) County business day period allowed for re-bid submission.

FCLV or DVBE TO COMPLETE:

Indicate ONE method for notification of re-bid opportunity by providing the appropriate e-mail address or Fax number.  Submit this document as a part of your quotation.

E-Mail Address or Fax Number (Identify contact person)

| STATEMENT OF LOCAL VENDOR CERTIFICATION COUNTY OF FRESNO |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Qualified local vendors desiring consideration under the Fresno County Local Vendor Preference must complete the following and submit with their quotation (print or type). |  |  |  |  |  |  |  |  |  |  |
| I |  |  |  |  |  | , |  |  |  |  |
|  | (individual submitting bid) |  |  |  |  |  | (title) |  |  |  |
| of/for |  |  |  | Certify that |  |  |  |  |  |  |
|  |  | (Company Name) |  |  |  |  |  | (Company Name) |  |  |
| Is a Fresno County local Vendor as defined within this RFQ and therefore qualifies for the Local Vendor Preference. |  |  |  |  |  |  |  |  |  |  |
| Signature |  |  |  |  | Title |  |  |  |  | Date |
| (Print Name) |  |  |  |  |  |  |  |  |  |  |

| STATEMENT OF DISABLED VETERAN BUSINESS ENTERPRISE CERTIFICATION |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Qualified vendors desiring consideration under the Fresno County DVBE Preference must complete the following and submit with their quotation (print or type). |  |  |  |  |  |  |  |  |  |  |  |
| I |  |  |  |  |  | , |  |  |  |  |  |
|  | (individual submitting bid) |  |  |  |  |  | (title) |  |  |  |  |
| of/for |  |  |  | Certify that |  |  |  |  |  |  |  |
|  |  | (*Company Name) |  |  |  |  |  | (Company Name) |  |  |  |
| Is a Disabled Veteran Business Enterprise certified by the State of California and therefore qualifies for the DVBE Preference. |  |  |  |  |  |  |  |  |  |  |  |
| State of California DVBE Certification Number: |  |  |  |  |  |  |  |  |  |  |  |
| Signature |  |  |  |  | Title |  |  |  |  |  | Date |
| (Print Name) |  |  |  |  |  |  |  |  |  |  |  |
| *Company name on file with the State of California DVBE program. |  |  |  |  |  |  |  |  |  |  |  |

- BIDDER TO COMPLETE THE FOLLOWING:

- PARTICIPATION

The County of Fresno is a member of the Central Valley Purchasing Group.  This group consists of Fresno, Kern, Kings, and Tulare Counties and all governmental, tax supported agencies within these counties.

Whenever possible, these and other tax supported agencies co-op (piggyback) on contracts put in place by one of the other agencies.

Any agency choosing to avail itself of this opportunity, will make purchases in their own name, make payment directly to the contractor, be liable to the contractor and vice versa, per the terms of the original contract, all the while holding the County of Fresno harmless.  If awarded this contract, please indicate whether you would extend the same terms and conditions to all tax supported agencies within this group as you are proposing to extend to Fresno County.

|  | Yes, we will extend contract terms and conditions to all qualified agencies within the Central Valley Purchasing Group and other tax supported agencies. |
| --- | --- |
|  | No, we will not extend contract terms to any agency other than the County of Fresno. |
| (Authorized Signature) |  |
| Title |  |

| Firm: |  |
| --- | --- |

REFERENCE LIST

Provide a list of at least five (5) customers for whom you have recently provided similar services.  Be sure to include all requested information.

| Reference Name: |  |  |  |  |  |  |  | Contact: |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Address: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| City: |  |  |  |  |  |  |  |  | State: |  |  |  |  | Zip: |  |  |  |
| Phone No.: |  | ( |  |  | ) |  | Date: |  |  |  |  |  |  |  |  |  |  |
| Service Provided: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Reference Name: |  |  |  |  |  |  |  | Contact: |  |  |  |  |  |  |  |  |  |
| Address: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| City: |  |  |  |  |  |  |  |  |  | State: |  |  |  |  | Zip: |  |  |
| Phone No.: |  | ( |  |  | ) |  | Date: |  |  |  |  |  |  |  |  |  |  |
| Service Provided: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Reference Name: |  |  |  |  |  |  |  | Contact: |  |  |  |  |  |  |  |  |  |
| Address: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| City: |  |  |  |  |  |  |  |  | State: |  |  |  |  | Zip: |  |  |  |
| Phone No.: |  | ( |  |  | ) |  | Date: |  |  |  |  |  |  |  |  |  |  |
| Service Provided: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Reference Name: |  |  |  |  |  |  |  | Contact: |  |  |  |  |  |  |  |  |  |
| Address: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| City: |  |  |  |  |  |  |  |  |  | State: |  |  |  |  | Zip: |  |  |
| Phone No.: |  | ( |  |  | ) |  | Date: |  |  |  |  |  |  |  |  |  |  |
| Service Provided: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Reference Name: |  |  |  |  |  |  |  | Contact: |  |  |  |  |  |  |  |  |  |
| Address: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| City: |  |  |  |  |  |  |  |  | State: |  |  |  |  | Zip: |  |  |  |
| Phone No.: |  | ( |  |  | ) |  | Date: |  |  |  |  |  |  |  |  |  |  |
| Service Provided: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Failure to provide a list of at least five (5) customers may be cause for rejection of this RFQ.

scope of work requirements/conditions/specifications

INTRODUCTION

The County of Fresno is soliciting bids to provide all labor, materials, equipment, etc., to perform maintenance, repair, inspection, programming and monitoring for the County’s fire and intrusion alarm systems.  The County of Fresno has approximately ninety-one (91) facilities with intrusion alarm systems, sixty (60) facilities with fire alarm systems, and thirty-eight (38) facilities that require monitoring services located throughout the County of Fresno.  The intent of this RFQ is to identify vendor(s) that are interested in performing contracted maintenance and repair services as well as quarterly, semi-annual, or annual inspections for fire alarm systems, annual inspections for intrusion alarm systems, testing of each of those systems, and monitoring of those facilities identified in the RFQ.  The County of Fresno’s delivery of service to the citizens and employees of the County is dependent upon the reliable operation of the identified systems.

OVERVIEW

This Request for Quotations provides information required to prepare and submit quotations for scheduled maintenance, annual, semi-annual, or quarterly inspections, repairs, and system monitoring.  The bidders shall submit information pertaining to their ability to perform the specified services in reliable, practical, cost-effective manner, while maintaining the highest technical standards regardless of the day or time.  The County has identified standards for new installations for both fire and intrusion alarm systems.  Any fire system that is no longer deemed reliable, has been deemed non-repairable, or has outlived its useful life will be replaced by a NOTIFIER system by Honeywell.  In addition any intrusion system that has been deemed unreliable, non-repairable, or has outlived its useful life will be replaced by a BOSCH intrusion system.  Bidder’s should demonstrate their knowledge and familiarity with all aspects of those systems.

COMPETENCE OF BIDDER

The importance of maintaining the identified equipment in a safe and efficient operating condition at all times demands that service be performed by a company who has satisfactorily maintained equipment of similar grade to the degree specified herein.

In order to demonstrate that the bidder can properly fulfill all of the services and conditions of these specifications, Contractor shall furnish with his bid a written statement indicating that he has:

- A current license to perform the work conformance with the provisions of the State business and Professions Code.  License Number shall be set forth in all bids and contracts.

- Satisfactorily preformed other contracts, of similar nature and magnitude.

- Adequate capital and satisfactory business standing as required by the work.

- The requisite organization of skilled and experienced technicians thoroughly trained in the inspection, testing, maintenance and repair of fire/duress system and device repair under his direct employment and supervision.

- The County has many NOTIFIER fire alarm systems.  The bidding organization shall be authorized by NOTIFIER to perform maintenance, testing, inspection and repair services, and shall employ technicians who are authorized by NOTIFIER to perform maintenance, testing, inspection and repair services to NOTIFIER fire alarm systems.

- In addition to the NOTIFIER alarm systems emplaced in County facilities, the County utilizes OnyxWorks as a redundant monitoring system to identify troubles with those systems.  The bidding organization must have skilled and experienced technicians who are authorized by NOTIFIER to program and troubleshoot the OnyxWorks system.

- The County utilizes a Bosch Connettix D6100i alarm receiver to monitor the intrusion alarms installed in County facilities.  This receiver utilizes both standard copper telephone lines and IP communication protocols.  Bidders wanting to bid on the intrusion alarm portion of this RFQ should demonstrate their ability to work with traditional systems utilizing standard copper pairs and the ability to program alarm systems utilizing IP communication.  In addition, those bidders will need to demonstrate the ability to use the ReadyKey Pro software for the D6100i as well as Remote Programming Software (RPS) for the Bosch systems installed.

- The necessary facilities and plant, including parts inventory located within fifty (50) miles distance from the County sites involved.

- Toll free communication facilities on a 24 hour-per-day, 365 days-per-year basis so his staff can be reached and will respond as specified herein.

- All proprietary information and diagnostic tools necessary to properly maintain, trouble shoot and adjust the County’s systems.

- The County understands that not every bidder will have expertise in every system installed in County facilities.  However, bidders must address which subcontractors will be used for those systems where the expertise is not sufficient for programming.  Systems that may be cause for a subcontractor for subcontractor work include, Gamewell, Edwards EST, Simplex-Grinnell, etc.  as well as gas suppression systems such as Sapphire, FM-200, and Halon as  listed in sections 2 and 3 of the quotation schedule.  Bidders that are planning on bidding on the NOTIFIER section of this RFQ must be authorized by NOTIFIER for repairs, maintenance, inspection, and programming.  Due to the fact that a majority of NOTIFIER systems are installed in the County’s high-rise facilities; subcontracted work on these systems is not acceptable.  In addition the County has several facilities that utilize legacy dual fire/intrusion systems.  Bidders should be competent to address those systems or have the means to use a subcontractor in cases that the technical issues are outside the expertise of the bidder.  Any subcontract work or agreements between the bidder and subcontractor will be subject to approval by the County and must meet all requirements contained within this RFQ.  Prices indicated on the quotation schedule must take into account whether the bidder will be subcontracting the work and will be subject to the RFQ requirements and any contract resulting from this RFQ.

- Listed in section 2 of the quotation schedule is building 700.  Building 700 is the Juvenile Justice Campus located at 3333 E.  American Ave.  Fresno Ca.  93725.  This campus consists of County facilities 701-712.  A majority of these facilities are considered detention facilities and thus are labeled as no-hostage facilities; meaning that employees will not bargain for the release of hostages.  In addition to the working environment, due to design and location of this facility, the Notifier system in these buildings experiences higher trouble rates with the smoke detectors in these facilities.  Technicians assigned to this area will spend an inordinate amount of time cleaning and replacing smoke detectors.  Technicians will be on call 24 hours per day due to the nature of this facility.

The above shall be included with the bidder’s quotation under the heading “Competence of Bidder.”

GENERAL REQUIREMENTS

Provide all labor, materials, appliances, tools, transportation, taxes, equipment, etc.  required to complete scheduled system maintenance, testing, inspection, and repair of all fire alarm systems.

Provide written quarterly or annual detailed inspection and testing reports to the Director of Internal Services or his/her designee within thirty (30) days of the completion of the testing and/or inspection.  Invoices for inspection and testing services will NOT be paid until inspection and testing reports are received and approved by the COUNTY.

All work shall be in full compliance with current rules and regulations of all applicable codes.  Nothing in this RFQ is to be construed to permit work not conforming to these codes.  Applicable codes and regulations include, but are not limited to, the following:

  - National Fire Protection Association - NFPA

  - Uniform Building Code (Latest Edition)

  - American Society of Mechanical Engineers - ASME

  - American Society for Testing and Materials - ASTM

  - National Electrical Code - NEC (Latest Edition)

  - National Electrical Manufacturer’s Association - NEMA

  - Title 24, Building Safety, C.C.R.

  - Occupational Safety and Health Act - OSHA

  - Underwriters Laboratory - UL

  - All Local Codes

COMMENCEMENT AND DURATION OF CONTRACT

Services to be performed under the contract(s) shall commence as specified and continue for a period of three (3) years with an option for two (2) additional one (1) year extensions.  The County may terminate any contract by giving the contractor thirty (30) days advance written notice of intent.

DIRECTOR OF INTERNAL SERVICES - RIGHTS AND RESPONSIBILITIES

The term “Director of Internal Services” shall refer to the Director of the Internal Services Department (ISD) of the County of Fresno or his agent acting for him in the supervision of any contract resulting from this RFQ.

It will be the duty of the Director of Internal Services to supervise the work as it progresses as well as to inspect materials which are used in the work.  The duty of inspectors acting under the Director of Internal Services shall not only report deviations from the specifications, but they shall have the power to stop the work pending a decision by the Director of Internal Services.  The inspector shall have no power to alter the specifications.  Advice or directions given to the Contractor by the inspector shall not be binding upon the Director of Internal Services; neither shall it release the Contractor from his responsibilities as herein stated.

It will be the right of the Director of Internal Services at any time to stop defective work or to stop the entire work by the Contractor if he is not complying with the rules, specifications, and contract entered into between the County of Fresno and the Contractor.

The Director of Internal Services shall have the right to require the Contractor to remove at any time any employee of the Contractor who shall be employed on this job and who appears to be incompetent, who acts in a disorderly, unsafe or improper manner, or fails to follow established protocols, including county rules and regulations and such person shall not again be put to work on this job without written consent of the Director of Internal Services.

The Director of Internal Services without invalidating the Contract, may order extra work or make changes by altering, adding to or deducting from the work only by written Orders, initiated by the Director of Internal Services or his/her agent and properly approved and authorized and setting forth the amount of money to be added or deducted.

DELIVERY REQUIREMENTS

The County of Fresno Internal Services Department - Security Division, will be responsible for the administration of the work requested under this Request for Quotation (RFQ), and shall be the Director of Internal Services designee for all work performed under the terms of any contract resulting from this RFQ.

Coordination and communication with the ISD Security Division will be essential to the successful completion of this work.  All facilities will remain in full normal operation for the duration of the agreement and any need for disruption of the services provided in these facilities shall be presented with the quotation.

Maintenance and any system component or parts replacement shall be approved by Director of Internal Services or his designee prior to the start of work and be so indicated in writing on the approved service form.

CONTROL OF WORK AND INSTRUCTIONS

The contractor shall provide diligent supervision of the work to the satisfaction of the Director of Internal Services.

Contractor shall confine storage of materials to such limits as may be directed by the Director of Internal Services and shall not unreasonably encumber the premises with materials and equipment.  Contractor shall enforce any instructions of the Director of Internal Services regarding signs, advertising, fire, danger signals, barricades, and smoking, and shall require all persons employed on the work to comply with all building regulations while on the premises.

SCHEDULING OF WORK

All maintenance service shall be scheduled subject to the review and approval of the Security Division.  The contractor(s) shall be required to provide yearly schedules of the work within 30 days of contract execution and on or before January 1, of the subsequent years.  These schedules must be adhered to throughout the term of the agreement.

No work shall interfere with the operation of the existing facilities on or adjacent to the site.  Normal Facility hours are, Monday to Friday, 7:00 AM to 6:00 PM

Work may be scheduled outside of normal working hours as approved by the Director of Internal Services.

Contractor shall provide for approval by the Director of Internal Services within 30 days of contract execution the contractors report of service form.  This form will be required to document services rendered.  The form at a minimum shall include, date of service, time of arrival/departure, printed name and signature of technician providing the service, building number, location in the building, type of service (preventative/corrective/extra services),   corrective action taken, location of devices serviced or repaired, parts utilization, status of service/repair, printed name and signature of County representative authorizing the work, completion of work County representative printed name and signature.

SAFEGUARDS

The Contractor shall provide, in conformity with all local codes and ordinances and as may be required, lock-outs, fences, guardrails, barricades, lights, danger signs, enclosures, etc.  and maintain such safeguards until work is complete.

Any fire hazardous operation shall have proper fire extinguisher, furnished by the contractor, close by and the adjacent area shall be policed before starting or stopping work for the day.  The contractor shall be responsible for all costs incurred by the County as a result of damage caused by the contractors operations, including costs associated with false fire alarms caused by the contractor.

The contractor shall ensure that the health and welfare of occupants of the building will not be effected by noise and fumes produced by the work.  The Director of Internal Services reserves the right to halt any work at any time he feels it adversely affects the building occupants.

Any asbestos removal shall be by the County.  If the contractor discovers asbestos, which has not been removed, the contractor shall immediately cease work in that area and promptly notify the Director of Internal Services or his representative.

MATERIALS & WORKMANSHIP

Materials and equipment shall be new unless otherwise approved by the Director of Internal Services.  Materials and equipment of a given type shall be of the same manufacture.  Materials and equipment shall be free of dents, scratches, marks, shipping tags, and all defacing features.

All material, equipment, devices, etc., shall be installed in accordance with the recommendations of the manufacture of the particular item.  The Contractor shall be responsible for all installations contrary to the manufacture’s recommendations.  The contractor shall make all necessary changes and revisions necessary for compliance.  Manufacturer’s installations instructions shall be delivered to and maintained on the job site through the duration of the project.

Any work which is done as an addition, expansion, or remodel to an existing system or system component shall be compatible with that system and be approved prior to the installation.

Workmanship shall be to the best of trade practices, performed by workers thoroughly trained and familiar with the respective systems.  NOTIFIER fire alarm systems shall be maintained and serviced by Technicians who are expressly authorized by NOTIFIER in the maintenance, testing, inspection, and repair of NOTIFIER fire alarm systems.  All defective workmanship shall be corrected by the contractor, at the contractor’s expense.

The contractor shall thoroughly clean all of his work, removing all debris, stain, and marks resulting from his work.  This includes but is not limited to building surfaces, piping, and equipment.  Surfaces shall be free of dirt, grease, labels, tags, tape, rust, and all foreign material.

Contractor shall ensure that before testing or servicing the systems notification is given to the appropriate County representative(s).  Contractor shall be responsible for all costs associated with alarms or signals that result in interruption of business or unplanned evacuation.

Wiring in panel boards, and cabinets shall be neatly installed.  Wiring shall be grouped, laced, or clipped and fanned out to wiring terminals.

Wiring in all cabinets, panel boards, control panels shall be identified and clearly marked at termination.

Installation of conduit, junction boxes, and associated equipment shall be done in a neat manner secured to the structure or suspended on conduit hangers.

All wiring and construction prints or diagrams of systems covered under this contract are the property of the County and upon termination of this contract shall be delivered to the Director of Internal Services.  Absolutely no changes are to be made to the circuitry or mechanical systems without prior approval of the Director of Internal Services.  Any changes without prior approval may be considered a breach of contract.  All changes in circuitry made by Contractor shall be properly recorded on the diagrams, including date of change and name of person making same.  It is the responsibility of the Contractor to maintain clean, legible, readable, and accurate schematics and wiring diagrams at all times.  Prints and diagrams are to remain on the job site.

RESPONSIBILITY OF CONTRACTOR

Contractor shall take responsibility for the work, and shall bear all losses resulting to him on account of the negligence of the Contractor.  Contractor shall be responsible for all work of subcontractors and shall assume the defense of and indemnify and save harmless the County of Fresno and any of its officers and their agents from claims of any kind arising from the negligent performance of this Contract by the Contractor or any of his subcontractors.  Contractor shall not be liable for injuries or damage to persons or property except those directly due to his own acts or omissions, and the responsibility of the County for injuries or damage to persons or property while on or about the equipment being maintained hereunder is in no way affected by this Agreement.  Contractor shall not be liable for any loss, damage, or delay caused by strikes, lock-outs, fire, explosion, theft, floods, riot, civil commotion, war, malicious mischief, act of God, or any cause beyond his reasonable control.

No equipment requiring repair shall be allowed to remain out of service due to the lack of diligent effort by the Contractor.  Any part or equipment locally available will be purchased locally if necessary to expedite the job.  Repairs shall be begun and carried to completion as soon as possible unless other arrangements are approved by the Director of Internal Services.

Contractor shall in no case allow the performance of work by subcontract unless the subcontractor has been approved by the Director of Internal Services, and in no case shall the use of subcontractors in any way alter the position of the Contractor or his sureties with relation to his Contract with County of Fresno.  When a subcontractor is used the responsibility for every portion of the work shall still remain with the Contractor.

Contractor shall obtain prior approval of the Director of Internal Services in writing for any area or space required for the Contractor’s storage during operations.  This space will be maintained in a clean and orderly fashion.

Materials, equipment, etc., shall not be piled or stored in any location which shall interfere with the conduct of the normal functions of the building or property.  All required safety precautions such as barricades, signs, danger signals, etc., shall be furnished and installed by the Contractor during operations.

Upon demand of the Director of Internal Services the Contractor shall correct any dangerous or hazardous situations that the Director of Internal Services may indicate.

Contractor shall completely protect against damage from either materials or equipment all surfaces, equipment and facilities, adjoining his work, including, but not limited to woodwork, walls, and floors.  All repair or replacement costs resulting from this damage shall be borne by the Contractor.  At the conclusion of each day’s work, the Contractor shall remove refuse, debris, or waste materials and leave the premises in an orderly condition as required by the Director of Internal Services.

Contractor must specify the degree of support the County may be required to furnish to accomplish the requirements of this agreement, if any.  Specify the man-hours required, and the nature of County’s participation within the scope of the agreement.

Contractor shall provide sufficient technicians for the service of the systems listed in this agreement in accordance with the specifications herein.  Technicians utilized for fire alarm systems shall be qualified and experienced in the inspection, testing, programming and maintenance of fire alarm systems.  Technicians utilized for intrusion alarm systems shall be qualified and experienced in the inspection, testing, programming and maintenance of intrusion alarm systems.  Contractor may be required at any time to provide substantiation and verification of qualifications of their employee(s) upon request of the Director of Internal Services.

Contractor shall provide, for approval by the Director of Internal Services, the procedure to be followed for requesting services provided in this agreement.  This procedure will include, method of requesting service, ability to provide estimated arrival time of technician to site, reporting of call completion, communication with requesting staff and technician servicing the contract, etc.

Contractor shall submit written quarterly, semi-annual, and annual inspection reports to the Director of Internal Services or his/her designee within thirty (30) calendar days of the actual date of the inspection.  Invoices for inspection and testing services will NOT be paid until inspection and testing reports are received and approved by the COUNTY.

EXTRA WORK - CHANGE IN WORK

The County, without invalidating the Contract, may order extra work or make changes by altering, adding to, or deducting from the work only by written Orders, initiated by the Director of Internal Services and properly approved and authorized and setting forth the amount of money to be added or deducted.

SPECIAL CONDITIONS

In the event that the County will withdraw any equipment from service, or the usefulness of any equipment shall end, during the term of this Contract, the Contractor shall agree to negotiate an acceptable reduction of cost for services for the balance of the duration of said Contract.

MANNER AND TIME OF CONDUCTING THE WORK

All work shall be performed by skilled fire/intrusion/duress system technicians and helpers directly employed and supervised by the Contractor.  Only qualified system technicians with a minimum of 4 years journeyman experience shall be allowed to perform service or maintenance work.  Helpers must work under the direct supervision of a journeyman technician.

Except for emergency callback service and minor repairs and/or adjustments hereinafter provided for, all work shall be performed during regular working hours and days.  Regular working hours are from 7:00 a.m.  until 6:00 p.m.  Monday through Friday.  County holidays excluded.

All equipment shutdowns for regular maintenance or extra examinations shall be scheduled in advance with the designated County representative and approved by the Director of Internal Services so as not to interfere with building operations during the peak usage times.  Shutdowns in excess of one hour may require scheduling outside of normal business hours.  No extra charges will be incurred because of a scheduled shutdown regardless of day or time.

EMERGENCY WORK

All work of a callback nature or trouble calls shall be treated as an emergency and work commenced shall be carried through to completion without delay.

Provide 24-hour emergency callback service for all equipment maintained hereunder.  Emergency callback service shall consist of prompt response to requests from the Director of Internal Services or his authorized representatives for emergency services on any day of the week, at any hour of the day or night.  An emergency call-back is defined as any necessity for maintenance, minor repair and/or adjustment of equipment between regular service calls to restore normal equipment operation.  Emergency call backs will be categorized as follows:

LEVEL I -  	Requires onsite response in one (1) hours or less.

LEVEL II - 	Requires onsite response in four (4) hours or less.

LEVEL III - 	Requires onsite response at 0700 hrs.  the next normal working day.

Determination of call level is at the sole discretion of the Director of Internal Services or his authorized representative.  Failure to furnish emergency call-back service within the above specified time of notification of need may result in termination of contract, withholding of payment, and/or another contractor to be hired to complete the work at the current contractor’s expense.

SERVICE REQUIREMENTS Fire alarm systems

FIRE ALARMS

FA-1	Conducted during normal hours.

*Quarterly:

Inspection and testing of 25% of all life safety devices in the facility including, but not limited to, smoke detectors, manual pull stations, duct type smoke detectors, magnetic hold open devices, duress signal devices, audible devices, visible devices, speakers, water flow devices, roll down doors, heat detectors, initiating devices, duress alarm pushbuttons, etc. per NFPA 72.

*Annually:

Annual inspections shall be coordinated with the County representative in conjunction with the required annual inspection by the Fresno City Fire Department when applicable.

Inspect and test all functions of the system including operation in various alarm and trouble modes in accordance with the manufacturer’s instructions.

Inspect and test all interfaced equipment per NFPA 72.

Check and replace standby batteries per NFPA 72.

Test and verify operation of trouble panel signals per NFPA 72.

Inspect and test remote annunciators per NFPA 72.

*One quarterly inspection and annual inspection to be performed during the same service call.

FA-2	Conducted after normal hours.

*Quarterly:

Inspection and testing of 25% of all life safety devices in the facility including, but not limited to, smoke detectors, manual pull stations, duct type smoke detectors, magnetic hold open devices, audible devices, duress signal devices, visible devices, speakers, water flow devices, roll down doors, heat detectors, initiating devices, duress alarm pushbuttons, etc. per NFPA 72.

*Annually:

Annual inspections shall be coordinated with the County representative in conjunction with the required annual inspection by the Fresno City Fire Department when applicable.

Inspect and test all functions of the system including operation in various alarm and trouble modes in accordance with the manufacturer’s instructions.

Inspect and test all interfaced equipment per NFPA 72.

Check and replace standby batteries per NFPA 72.

Test and verify operation of trouble panel signals per NFPA 72.

Inspect and test remote annunciators per NFPA 72.

*One quarterly inspection and annual inspection to be performed during the same service call.

FA-3	Conducted during normal hours.

Annually:

Annual inspections shall be coordinated with the County representative in conjunction with the required annual inspection by the Fresno City Fire Department when applicable.

Inspection and testing of all life safety devices in the facility including, but not limited to, smoke detectors, manual pull stations, duct type smoke detectors, magnetic hold open devices, audible devices, duress signal devices, visible devices, speakers, water flow devices, roll down doors, heat detectors, initiating devices, duress alarm pushbuttons, etc.  per NFPA 72.

Inspect and test all functions of the system including operation in various alarm and trouble modes in accordance with the manufacturer’s instructions.

Inspect and test all interfaced equipment per NFPA 72.

Check and replace standby batteries per NFPA 72.

Test and verify operation of trouble panel signals per NFPA 72.

Inspect and test remote annunciators per NFPA 72.

FA-4	Conducted after normal hours.

Annually:

Annual inspections shall be coordinated with the County representative in conjunction with the required annual inspection by the Fresno City Fire Department when applicable.

Inspection and testing of all life safety devices in the facility including, but not limited to, smoke detectors, manual pull stations, duct type smoke detectors, magnetic hold open devices, audible devices, duress signal devices, visible devices, speakers, water flow devices, roll down doors, heat detectors, initiating devices, duress alarm pushbuttons, etc.  per NFPA 72.

Inspect and test all functions of the system including operation in various alarm and trouble modes in accordance with the manufacturer’s instructions.

Inspect and test all interfaced equipment per NFPA 72.

Check and replace standby batteries per NFPA 72.

Test and verify operation of trouble panel signals per NFPA 72.

Inspect and test remote annunciators per NFPA 72.

SPECIAL HAZARD EQUIPMENT

SHE-1	Conducted during normal hours.

Semi-annual testing and inspection of Special Hazard Systems per NFPA 72; Equipment shall include but not be limited to pre-action and deluge sprinkler, Halon systems, FM-200 systems, and dry chemical systems.

DIGITAL ALARM COMMUNICATOR TRANSMITTERS RECEIVERS

- DACT-1 Conducted during normal hours.

Provide, maintain, and monitor Digital Alarm Communicator Transmitters 	and Receivers per NFPA 72.

TEMPERATURE SENSING DEVICES

TSD-1	Conducted during normal hours.

Provide annual inspection and testing of identified devices.

DEVICE COUNTS

990-5161 Device Counts.pdf

BIDDER TO COMPLETE (FIRE SYSTEMS)

Bidder shall list all subcontractors that would perform work in excess of one/half of one percent of the total amount of your bid, and state general type of work such subcontractor would be performing:

| Bidder’s Company Name: |  |
| --- | --- |
| Authorized Signature: |  |
| Print Name and Title: |  |

CONTRACTOR'S LICENSE:

Bidder to possess appropriate license for the project in accordance with current regulations/statutes.

The vendor shall possess a current State of California contractor’s License, Class C-7 (Low Voltage system Contractor) or another license class that covers the work to be performed.  The proposal must indicate the license held by the bidder, which enables him/her to perform the work.

If the license is other than a Class C-7, the bidder must explain why his/her license(s) is acceptable.  The County will review and determine if acceptable.

| Number and Class: |  |
| --- | --- |
| Date of Issue: |  |

- The Prevailing Wage rates for work performed under the ensuing agreement shall be those rates indicated on the attached (section 1) “General Prevailing Wage Determination” No.  FRE-2013-1 under the Craft Classifications of “Comm & System Installer” and “Inside Wireman”.

- PRICING OPTIONS:  Bidders may bid on either a firm price option (Option One) or escalated price option (Option Two), subject to the provisions below.  Bidder to indicate which price option shall apply to his/her bid (bid shall be evaluated on Option One if not indicated).

The following provisions shall apply to the price options:

- Option One - Firm Price

All prices quoted shall be firm for the contract period.  No price increase shall be permitted.

- Option Two - Escalated Price

- Prices quoted shall be firm for a minimum of one year commencing on the ensuing agreement’s effective date.

- The contractor may request a price escalation once every twelve months commencing upon completion of the agreements first one year period.  The contractor must submit his/her requested price escalation in writing, to the County of Fresno- Purchasing Division not earlier than sixty (60) days prior to agreement’s anniversary date.  The extent of a requested price increase shall be limited to actual increases to direct costs experienced by the contractor and shall be only for the purpose of recovering such additional costs of doing business; a requested price escalation shall be subject to a five percent (5%) maximum; a requested price escalation shall not include an additional profit margin.  A requested price escalation shall include third party substantiation as evidence of the contractor’s increased costs (e.g.  prevailing wage documentation, changes in published market indicators for the industry, cost data for materials, supplies and products necessary to the contract, etc.  and any other substantiating information as requested by the County of Fresno).  The effective date of any requested price increase must be a minimum of twelve (12) months from the effective date of the most recent price increase.

The maximum allowable annual price escalation shall be five percent (5%).  The bidder may offer an escalation of less than five percent under the “BIDDER TO COMPLETE” section below.  Vendor quotations selecting the Price Escalation option shall be evaluated using the maximum annual percentage increase for years two and three of the contract.

- The notice of a proposed price escalation must be submitted to the County of Fresno Purchasing Division a minimum of sixty (60) days prior to the effective date of the requested price increase.

- Upon receipt of price escalation notice, the County of Fresno reserves the right to either:

- Accept the price escalation notice as competitive with the general market price at that time, effective a minimum of sixty (60) days from receipt of an acceptable notice; or

- Cancel the agreement without prejudice.

- A written acknowledgment of acceptance or denial will be provided in response to each price escalation request.

- No price increase shall apply to services ordered from the contract prior to the effective date of the price increase.

BIDDER TO COMPLETE AND RETURN AS PART OF THEIR QUOTATION:

- PRICE OPTIONS

Bidders may bid on either a firm price option or escalated price option, subject to the provisions below.  Bidders to indicate which price option shall apply to their bid by checking the appropriate line below.

| OPTION ONE: * ( ) FIRM PRICE | (No price increase for three (3) year contract period.) |
| --- | --- |
| OPTION TWO: * ( ) ESCALATED PRICE | (Price changes will be on an annual basis for the life of contract, subject to the stated conditions.) |

* Check the appropriate option.

- MAXIMUM PRICE ESCALATOR:

The maximum annual price increase allowed by the County is five percent (5%) and is subject to the conditions stated above.

| The maximum annual price increase offered by the bidder is |  | (%) *Percent. |
| --- | --- | --- |
|  | Bidder to state percentage |  |

  - This must be stated as a numeric value only (i.e.  one percent (1%), two percent (2%), two and one-half percent (2 ½%) etc.)

Vendor must complete and return with Quotation.

SERVICE REQUIREMENTS intrusion alarm systems and alarm monitoring services

- DIGITAL ALARM COMMUNICATOR TRANSMITTERS RECEIVERS

- DACT-1 Conducted during normal hours.

Provide, maintain, and monitor Digital Alarm Communicator Transmitters 	and Receivers per NFPA 72.

- TEMPERATURE SENSING DEVICES

TSD-1	Conducted during normal hours.

Provide annual inspection and testing of identified devices.

- INTRUSION ALARM

- Conducted during normal hours.

Annual preventative maintenance of intrusion alarms systems shall at minimum include the following:

  - Check all zip plates for proper operation and stability.

  - Check all line voltage connections.

  - Replace standby batteries as necessary.

  - Clean interior and exterior of enclosures.

  - Test operation of all digital dialers and line test features.

  - Inspect alarm cables for damage.

  - Check operation and align photo-electric cells.

  - Check operation and adjust all door/window contacts as necessary.

  - Walk test all sonic detection sensors/systems for serviceability and make necessary adjustments.

  - Test all interior and exterior microwave system operation and adjust to manufacturer’s specifications as required.

- Conducted after normal hours.

Annual preventative maintenance of intrusion alarms systems shall at minimum include the following:

  - Check all zip plates for proper operation and stability.

  - Check all line voltage connections.

  - Replace standby batteries as necessary.

  - Clean interior and exterior of enclosures.

  - Test operation of all digital dialers and line test features.

  - Inspect alarm cables for damage.

  - Check operation and align photo-electric cells.

  - Check operation and adjust all door/window contacts as necessary.

  - Walk test all sonic detection sensors/systems for serviceability and make necessary adjustments.

  - Test all interior and exterior microwave system operation and adjust to manufacturer’s specifications as required.

- Conducted during normal hours.

  - Pertains specifically to Closed-Circuit Television installed on the 1st Floor of the Hall of      Records, room 105, building 603.  2281 Tulare Street.

  - Equipment to be inspected

| (1) | Dedicated Micros BX2 Digital Video Recorder (DVR) |
| --- | --- |
| (1) | Dedicated Micros JBODIT External Hard Drive |
| (1) | Dedicated Micros KBS3A Keyboard |
| (1) | Tripplite UPS |
| (1) | Pelco Camera Power Supply |
| (1) | Pelco 21” Color Monitor |
| (8) | Pelco Color Cameras |

BIDDER TO COMPLETE (INTRUSION SYSTEMS)

IF A SUBCONTRACTOR WILL BE USED TO COMPLETE WORK ON INTRUSION SYSTEMS

Bidder shall list all subcontractors that would perform work in excess of one/half of one percent of the total amount of your bid, and state general type of work such subcontractor would be performing:

| Bidder’s Company Name: |  |
| --- | --- |
| Authorized Signature: |  |
| Print Name and Title: |  |

Following shall be inserted in its place:

CONTRACTOR'S LICENSE:

Bidder to possess appropriate license for the project in accordance with current regulations/statutes.

The vendor shall possess a current State of California contractor’s License, Class C-7 (Low Voltage system Contractor) or another license class that covers the work to be performed.  The proposal must indicate the license held by the bidder, which enables him/her to perform the work.

If the license is other than a Class C-7, the bidder must explain why his/her license(s) is acceptable.  The County will review and determine if acceptable.

| Number and Class: |  |
| --- | --- |
| Date of Issue: |  |

The Prevailing Wage rates for work performed under the ensuing agreement shall be those rates indicated on the attached (section 1) “General Prevailing Wage Determination” No. FRE-2013-1 under the Craft Classifications of “Comm & System Installer”.

PRICING OPTIONS:  Bidders may bid on either a firm price option (Option One) or escalated price option (Option Two), subject to the provisions below.  Bidder to indicate which price option shall apply to his/her bid (bid shall be evaluated on Option One if not indicated).

The following provisions shall apply to the price options:

- Option One - Firm Price

All prices quoted shall be firm for the contract period.  No price increase shall be permitted.

- Option Two - Escalated Price

  - Prices quoted shall be firm for a minimum of one year commencing on the ensuing agreement’s effective date.

  - The contractor may request a price escalation once every twelve months commencing upon completion of the agreements first one year period.  The contractor must submit his/her requested price escalation in writing, to the County of Fresno- Purchasing Division not earlier than sixty (60) days prior to agreement’s anniversary date.  The extent of a requested price increase shall be limited to actual increases to direct costs experienced by the contractor and shall be only for the purpose of recovering such additional costs of doing business; a requested price escalation shall be subject to a five percent (5%) maximum; a requested price escalation shall not include an additional profit margin.  A requested price escalation shall include third party substantiation as evidence of the contractor’s increased costs (e.g.  prevailing wage documentation, changes in published market indicators for the industry, cost data for materials, supplies and products necessary to the contract, etc.  and any other substantiating information as requested by the County of Fresno).  The effective date of any requested price increase must be a minimum of twelve (12) months from the effective date of the most recent price increase.

The maximum allowable annual price escalation shall be five percent (5%).  The bidder may offer an escalation of less than five percent under the “BIDDER TO COMPLETE” section below.  Vendor quotations selecting the Price Escalation option shall be evaluated using the maximum annual percentage increase for years two and three of the contract.

  - The notice of a proposed price escalation must be submitted to the County of Fresno Purchasing Division a minimum of sixty (60) days prior to the effective date of the requested price increase.

  - Upon receipt of price escalation notice, the County of Fresno reserves the right to either:

    - Accept the price escalation notice as competitive with the general market price at that time, effective a minimum of sixty (60) days from receipt of an acceptable notice; or

    - Cancel the agreement without prejudice.

  - A written acknowledgment of acceptance or denial will be provided in response to each price escalation request.

  - No price increase shall apply to services ordered from the contract prior to the effective date of the price increase.

BIDDER TO COMPLETE AND RETURN AS PART OF THEIR QUOTATION:

- PRICE OPTIONS

Bidders may bid on either a firm price option or escalated price option, subject to the provisions below.  Bidders to indicate which price option shall apply to their bid by checking the appropriate line below.

| OPTION ONE: * ( ) FIRM PRICE | (No price increase for three (3) year contract period.) |
| --- | --- |
| OPTION TWO: * ( ) ESCALATED PRICE | (Price changes will be on an annual basis for the life of contract, subject to the stated conditions.) |

* Check the appropriate option.

- MAXIMUM PRICE ESCALATOR:

The maximum annual price increase allowed by the County is five percent (5%) and is subject to the conditions stated above.

| The maximum annual price increase offered by the bidder is |  | (%) *Percent. |
| --- | --- | --- |
|  | Bidder to state percentage |  |

  - This must be stated as a numeric value only (i.e.  one percent (1%), two percent (2%), two and one-half percent (2 ½%) etc.)

Vendor must complete and return with Quotation.

QUOTATION SCHEDULE (FIRE ALARM SYSTEMS)

All labor, materials, appliances, tools, transportation, taxes, equipment, etc.  to provide scheduled maintenance, corrective maintenance and monitoring, as specified herein.

NOTE:  The “Service Descriptions” as stated on the Quotation Schedules indicate the scope of services to be provided at each location.  Refer to the appropriate service designation (i.e.  FA-1, FA-2, etc.), as stated under the “SERVICE REQUIREMENTS” section of this RFQ, for specifics.

QUOTATION SCHEDULE (FIRE ALARM SYSTEMS)
EMERGENCY SERVICES

Bidder to quote hourly labor rates for emergency service.  The service levels (I, II and III) are as previously defined under the ‘EMERGENCY WORK” section of this RFQ.

|  | LEVEL I |  | LEVEL II |  | LEVEL III |  |
| --- | --- | --- | --- | --- | --- | --- |
| Technician Type | *Regular Time | **Over- Time | Regular Time | Over- Time | Regular Time | Over- Time |
| Journeymen | $ /hr | $ /hr | $ /hr | $ /hr | $ /hr | $ /hr |
| * | $ | $ | $ | $ | $ | $ |
| * | $ | $ | $ | $ | $ | $ |

Indicate when hourly charge begins and ends and the smallest portion of an hour for which a charge will be made.

*	If other than journeymen state type and define below.

**	Define regular time and overtime in the space provided below.  Indicate and define rates other than regular and overtime that might apply.

Indicate below any minimum charges that would apply to emergency services.

OTHER CHARGES

Charges for services other than those specified under this RFQ.

Labor Rates

State hourly labor rate for each type of technician (i.e.  apprentice, journeyman, etc.) for each category of work hours (i.e.  standard time, overtime, holidays, etc.).  Attach a description of each technician type (training and duties) and define each category of work hours.

| TECHNICIAN TYPE |  | WORK HOUR CATEGORY |  | HOURLY RATE |
| --- | --- | --- | --- | --- |

Indicate when hourly charge begins and ends and the smallest portion of an hour for which a charge will be made.

Parts Price List

*List commonly used repair parts and indicate contract price.

| DESCRIPTION |  | BRAND & PART NUMBER |  | PRICE |
| --- | --- | --- | --- | --- |

*Use an attachment for additional items.

State method for determining cost of parts and materials not indicated above (i.e.  cost plus, list price less?%, etc.).

OTHER CHARGES (cont)

Miscellaneous

State all other charges that may at some time be applicable.

.

QUOTATION SCHEDULE 
(INTRUSION ALARM SYSTEMS)
EMERGENCY SERVICES

Bidder to quote hourly labor rates for emergency service.  The service levels (I, II and III) are as previously defined under the ‘EMERGENCY WORK” section of this RFQ.

|  | LEVEL I |  | LEVEL II |  | LEVEL III |  |
| --- | --- | --- | --- | --- | --- | --- |
| Technician Type | *Regular Time | **Over- Time | Regular Time | Over- Time | Regular Time | Over- Time |
| Journeymen | $ /hr | $ /hr | $ /hr | $ /hr | $ /hr | $ /hr |
| * | $ | $ | $ | $ | $ | $ |
| * | $ | $ | $ | $ | $ | $ |

Indicate when hourly charge begins and ends and the smallest portion of an hour for which a charge will be made.

*	If other than journeymen state type and define below.

**	Define regular time and overtime in the space provided below.  Indicate and define rates other than regular and overtime that might apply.

Indicate below any minimum charges that would apply to emergency services.

OTHER CHARGES

Charges for services other than those specified under this RFQ.

Labor Rates

State hourly labor rate for each type of technician (i.e.  apprentice, journeyman, etc.) for each category of work hours (i.e.  standard time, overtime, holidays, etc.).  Attach a description of each technician type (training and duties) and define each category of work hours.

| TECHNICIAN TYPE |  | WORK HOUR CATEGORY |  | HOURLY RATE |
| --- | --- | --- | --- | --- |

Indicate when hourly charge begins and ends and the smallest portion of an hour for which a charge will be made.

Parts Price List

*List commonly used repair parts and indicate contract price.

| DESCRIPTION |  | BRAND & PART NUMBER |  | PRICE |
| --- | --- | --- | --- | --- |

*Use an attachment for additional items.

State method for determining cost of parts and materials not indicated above (i.e.  cost plus, list price less?%, etc.).

OTHER CHARGES (cont)

Miscellaneous

State all other charges that may at some time be applicable.

SECTION 1 PREVAILING WAGE RATES FRESNO COUNTY FRE-2013-1 990-5161 Sec 1 - Prevailing Wage Rates FC FRE-2013-1.pdf

SECTION 2 Notifier Systems 990-5161 Sec 2 - Notifier Systems.pdf

SECTION 3 General Fire Alarm Systems 990-5161 Sec 3 - General Fire Alarm Systems.pdf

SECTION 4 Intrsion Alarm System 990-5161 Sec 4 - Intrusion Alarm Systems.pdf

SECTION 5 Fire Alarm Monitoring 990-5161 Sec 5 - Fire Alarm Monitoring.pdf

CHECK LIST

This Checklist is provided to assist the vendors in the preparation of their bid response.  Included in this list, are important requirements, and is the responsibility of the bidder to submit with the bid package in order to make the bid compliant.  Because this checklist is just a guideline, the bidder must read and comply with the bid in its entirety.

Check off each of the following:

|  |  | The Request for Quotation (RFQ) has been signed and completed. |
| --- | --- | --- |
|  |  | One (1) original and two (2) copies of the RFQ have been provided. |
|  |  | Addenda, if any, have been completed, signed, and included in the bid package. |
|  |  | The completed Reference List as provided with this RFQ. |
|  |  | The Quotation Schedule as provided with this RFQ has been completed, priced reviewed for accuracy and any corrections initialed in ink. |
|  |  | Indicate all of bidder exceptions to the County’s requirements, conditions, and specifications as stated within this RFQ. |
|  |  | Bidder to Complete page as provided with this RFQ. |
|  |  | Lastly, on the LOWER LEFT HAND CORNER of the sealed envelope, box, etc. transmitting your bid include the following information: |

| County of Fresno RFQ No. |  |  | 990-5161 |
| --- | --- | --- | --- |
| Closing Date: | June 27, 2013 |  |  |
| Closing Time: | 2:00 P.M. |  |  |
| Commodity or Service: |  |  |  |

This Checklist does not need to be returned with your bid.