| COUNTY OF FRESNO |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Request for QUOTATION |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | NUMBER: 285-4894 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| February 7, 2011 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ORG/Requisition: 8935/ 1321001085 |  |  |  |  |  |  | PURCHASING USE |  |  |  | /tmp/in/input.doc |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | JEB |  |  |  |  |  |  |  |  |  |  |  |
| IMPORTANT: SUBMIT QUOTATION IN SEALED PACKAGE WITH QUOTATION NUMBER, CLOSING DATE AND BUYER’S NAME MARKED CLEARLY ON THE OUTSIDE TO: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| COUNTY OF FRESNO, Purchasing 4525 EAST HAMILTON AVENUE, 2nd Floor FRESNO, CA 93702-4599 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Closing date of bid will be at 2:00 p.m., on March 9, 2011. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| QUOTATIONS WILL BE CONSIDERED LATE WHEN THE OFFICIAL PURCHASING TIME CLOCK READS 2:00 P.M. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Quotations will be opened and publicly read at that time. All quotation information will be available for review after contract award. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Clarifications of specifications are to be directed to: Craig Nickel, e-mail CountyPurchasing@co.fresno.ca.us, phone (559) 456-7110, or fax (559) 456-7831. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| GENERAL CONDITIONS: See “County Of Fresno Purchasing Standard Instructions And Conditions For Request For Proposals (RFP’S) and Requests for Quotations (RFQ’S)” attached. Check County of Fresno Purchasing’s Open Solicitations website at http://www2.co.fresno.ca.us/0440/Bidshome2.asp for RFQ/RFP documents and changes. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| BIDDER TO COMPLETE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| UNDERSIGNED AGREES TO FURNISH THE COMMODITY OR SERVICE STIPULATED IN THE ATTACHED QUOTATION SCHEDULE AT THE PRICES AND TERMS STATED, SUBJECT TO THE “COUNTY OF FRESNO PURCHASING STANDARD INSTRUCTIONS AND CONDITIONS FOR REQUEST FOR QUOTATIONS (RFP’S) AND REQUESTS FOR QUOTATIONS (RFQ’S)”ATTACHED. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Except as noted on individual items, the following will apply to all items in the Quotation Schedule. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Complete delivery will be made within |  |  |  |  |  |  |  | calendar days after receipt of Order. |  |  |  |  |  |  |  |  |  |  |
| - A cash discount of |  |  |  |  | % |  |  |  |  | days will apply. |  |  |  |  |  |  |  |  |
| Company |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Address |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| City |  |  |  |  |  |  |  |  |  |  |  |  | State |  | Zip Code |  |  |  |
| ( ) |  |  |  | ( ) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Telephone Number |  |  |  | Facsimile Number |  |  |  |  |  |  |  |  | E-mail Address |  |  |  |  |  |
| Signed By |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Print Name |  |  |  |  |  |  |  |  | Title |  |  |  |  |  |  |  |  |  |

COUNTY OF FRESNO PURCHASING

STANDARD INSTRUCTIONS AND CONDITIONS FOR
REQUESTS FOR PROPOSALS (RFP'S) AND REQUESTS FOR QUOTATIONS (RFQ'S)

Note: the reference to “bids” in the following paragraphs applies to RFP's and RFQ's

## GENERAL CONDITIONS

By submitting a bid the bidder agrees to the following conditions.  These conditions will apply to all subsequent purchases based on this bid.

- BID PREPARATION:

  - All prices and notations must be typed or written in ink.  No erasures permitted.  Errors may be crossed out, initialed and corrections printed in ink by person signing bid.

  - Brand Names: Brand names and numbers when given are for reference. Equal items will be considered, provided the offer clearly describes the article and how it differs from that specified.  In the absence of such information it shall be understood the offering is exactly as specified.

  - State brand or make of each item.  If bidding on other than specified, state make, model and brand being bid and attach supporting literature/specifications to the bid.

  - Bid on each item separately.  Prices should be stated in units specified herein.  All applicable charges must be quoted; charges on invoice not quoted herein will be disallowed.

  - Time of delivery is a part of the consideration and must be stated in definite terms and must be adhered to.  F.O.B. Point shall be destination or freight charges must be stated.

  - All bids must be dated and signed with the firm’s name and by an authorized officer or employee.

  - Unless otherwise noted, prices shall be firm for one hundred eighty (180) days after closing date of bid.

- SUBMITTING BIDS:

  - Each bid must be submitted on forms provided in a sealed envelope/package with bid number and closing date and time on the outside of the envelope/package.

  - Interpretation: Should any discrepancies or omissions be found in the bid specifications or doubt as to their meaning, the bidder shall notify the Buyer in writing at once.  The County shall not be held responsible for verbal interpretations.  Questions regarding the bid must be received by Purchasing at least five (5) working days before bid opening.  All addenda issued shall be in writing, duly issued by Purchasing and incorporated into the contract.

  - ISSUING AGENT/AUTHORIZED CONTACT: This RFP/RFQ has been issued by County of Fresno, Purchasing. Purchasing shall be the vendor’s sole point of contact with regard to the RFP/RFQ, its content, and all issues concerning it.

All communication regarding this RFP/RFQ shall be directed to an authorized representative of County Purchasing. The specific buyer managing this RFP/RFQ is identified on the cover page, along with his or her telephone number, and he or she should be the primary point of contact for discussions or information pertaining to the RFP/RFQ. Contact with any other County representative, including elected officials, for the purpose of discussing this RFP/RFQ, its content, or any other issue concerning it, is prohibited unless authorized by Purchasing. Violation of this clause, by the vendor having unauthorized contact (verbally or in writing) with such other County representatives, may constitute grounds for rejection by Purchasing of the vendor’s quotation.

The above stated restriction on vendor contact with County representatives shall apply until the County has awarded a purchase order or contract to a vendor or vendors, except as follows. First, in the event that a vendor initiates a formal protest against the RFP/RFQ, such vendor may contact the appropriate individual, or individuals who are managing that protest as outlined in the County’s established protest procedures. All such contact must be in accordance with the sequence set forth under the protest procedures. Second, in the event a public hearing is scheduled before the Board of Supervisors to hear testimony prior to its approval of a purchase order or contract, any vendor may address the Board.

  - Bids received after the closing time will NOT be considered.

  - Bidders are to bid what is specified or requested first. If unable to or unwilling to, bidder may bid alternative or option, indicating all advantages, disadvantages and their associated cost.

  - Public Contract Code Section 7028.15

Where the State of California requires a Contractor’s license, it is a misdemeanor for any person to submit a bid unless specifically exempted.

- FAILURE TO BID:

  - If not bidding, return bid sheet and state reason for no bid or your name may be removed from mailing list.

- TAXES, CHARGES AND EXTRAS:

  - County of Fresno is subject to California sales and/or use tax (8.975%). Please indicate as a separate line item if applicable.

  - DO NOT include Federal Excise Tax.  County is exempt under Registration No. 94-73-03401-K.

  - County is exempt from Federal Transportation Tax.  Exemption certificate is not required where shipping papers show consignee as County of Fresno.

  - Charges for transportation, containers, packing, etc. will not be paid unless specified in bid.

- W-9 – REQUEST FOR TAXPAYER IDENTIFICATION NUMBER AND CERTIFICATION:

Upon award of bid, the vendor shall submit to County Purchasing, a completed W-9 - Request for Taxpayer Identification Number and Certification if not already a current vendor with The County of Fresno. This form is available from the IRS to complete on line at http://www.irs.gov/pub/irs-pdf/fw9.pdf.

- AWARDS:

  - Subject to the local preference provisions referenced in Paragraph 7 below and more thoroughly set forth in the General Requirements section of this RFP/RFQ, award(s) will be made to the most responsive responsible bidder.  The evaluation will include such things as life-cycle cost, availability, delivery costs and whose product and/or service is deemed to be in the best interest of the County. The County shall be the sole judge in making such determination.

  - Unless bidder gives notice of all-or-none award in bid, County may accept any item, group of items or on the basis of total bid.

  - The County reserves the right to reject any and all bids and to waive informalities or irregularities in bids.

  - Award Notices are tentative: Acceptance of an offer made in response to this RFP/RFQ shall occur only upon execution of an agreement by both parties or issuance of a valid written Purchase Order by Fresno County Purchasing.

  - After award, all bids shall be open to public inspection. The County assumes no responsibility for the confidentiality of information offered in a bid.

- LOCAL VENDORS:

  - Local Vendor Preference (applicable to RFQ Process only)

The following provisions are applicable only to the County’s acquisition of materials, equipment or supplies through the RFQ process when the funding source does not require an exemption to the Local Vendor Preference.

THE PROVISIONS OF THIS PARAGRAPH ARE APPLICABLE, NOTWITHSTANDING ANY OTHER PROVISIONS OF THIS RFQ TO THE CONTRARY

If the apparent low bidder is not a local vendor, any local vendor who submitted a bid which was within five percent (5%) of the lowest responsive  bid as determined by the purchasing agent shall have the option of submitting a new bid within forty-eight (48) hours (not including weekends and holidays) of County’s delivery of notification. Such new bids must be in an amount less than or equal to the lowest responsive bid as determined by the purchasing agent.  If the purchasing agent receives any new bids from local vendors who have the option of submitting new bids within said forty-eight (48) hour period, it shall award the contract to the local vendor submitting the lowest responsible bid. If no new bids are received, the contract shall be awarded to the original low bidder as announced by the purchasing agent.

  - Local Vendor Defined

“Local Vendor” shall mean any business which:

- Has its headquarters, distribution point or locally-owned franchise located in or having a street address within the County for at least six (6) months immediately prior to the issuance of the request for competitive bids by the purchasing agent; and

- Holds any required business license by a jurisdiction located in Fresno County; and

- Employs at least one (1) full-time or two (2) part-time employees whose primary residence is located within Fresno County, or if the business has no employees, shall be at least fifty percent (50%) owned by one or more persons whose primary residence(s) is located within Fresno County.

- TIE BIDS:

All other factors being equal, the contract shall be awarded to the Fresno County vendor or, if neither or both are Fresno County vendors, it may be awarded by the flip of a coin in the presence of witnesses or the entire bid may be rejected and re-bid. If the General Requirements of this RFP/RFQ state that they are applicable, the provisions of the Fresno County Local Vendor Preference shall take priority over this paragraph.

- PATENT INDEMNITY:

The vendor shall hold the County, its officers, agents and employees, harmless from liability of any nature or kind, including costs and expenses, for infringement or use of any copyrighted or uncopyrighted composition, secret process, patented or unpatented invention, article or appliance furnished or used in connection with this bid.

- SAMPLES:

Samples, when required, must be furnished and delivered free and, if not destroyed by tests, will upon written request (within thirty (30) days of bid closing date) be returned at the bidder's expense. In the absence of such notification, County shall have the right to dispose of the samples in whatever manner it deems appropriate.

- RIGHTS AND REMEDIES OF COUNTY FOR DEFAULT:

  - In case of default by vendor, the County may procure the articles or service from another source and may recover the cost difference and related expenses occasioned thereby from any unpaid balance due the vendor or by proceeding against performance bond of the vendor, if any, or by suit against the vendor. The prices paid by the County shall be considered the prevailing market price at the time such purchase is made.

  - Articles or services, which upon delivery inspection do not meet specifications, will be rejected and the vendor will be considered in default. Vendor shall reimburse County for expenses related to delivery of non-specified goods or services.

  - Regardless of F.O.B. point, vendor agrees to bear all risks of loss, injury or destruction to goods and materials ordered herein which occur prior to delivery and such loss, injury or destruction shall not release vendor from any obligation hereunder.

- DISCOUNTS:

Terms of less than fifteen (15) days for cash payment will be considered as net in evaluating this bid. A discount for payment within fifteen (15) days or more will be considered in determining the award of bid. Discount period will commence either the later of delivery or receipt of invoice by the County. Standard terms are Net forty-five (45) days.

- SPECIAL CONDITIONS IN BID SCHEDULE SUPERSEDE GENERAL CONDITIONS:

The “General Conditions” provisions of this RFP/RFQ shall be superseded if in conflict with any other section of this bid, to the extent of any such conflict.

- SPECIAL REQUIREMENT:

With the invoice or within twenty-five (25) days of delivery, the seller must provide to the County a Material Safety Data Sheet for each product, which contains any substance on “The List of 800 Hazardous Substances”, published by the State Director of Industrial Relations. (See Hazardous Substances Information and Training Act. California State Labor Code Sections 6360 through 6399.7.)

- RECYCLED PRODUCTS/MATERIALS:

Vendors are encouraged to provide and quote (with documentation) recycled or recyclable products/materials which meet stated specifications.

- YEAR COMPLIANCE WARRANTY:

Vendor warrants that any product furnished pursuant to this Agreement/order shall support a four-digit year format and be able to accurately process date and time data from, into and between the twentieth and twenty-first centuries, as well as leap year calculations. "Product" shall include, without limitation, any piece or component of equipment, hardware, firmware, middleware, custom or commercial software, or internal components or subroutines therein. This warranty shall survive termination or expiration of this Agreement.

In the event of any decrease in product functionality or accuracy related to time and/or date data related codes and/or internal subroutines that impede the product from operating correctly using dates beyond December 31, 1999, vendor shall restore or repair the product to the same level of functionality as warranted herein, so as to minimize interruption to County's ongoing business process, time being of the essence. In the event that such warranty compliance requires the acquisition of additional programs, the expense for any such associated or additional acquisitions, which may be required, including, without limitation, data conversion tools, shall be borne exclusively by vendor. Nothing in this warranty shall be construed to limit any rights or remedies the County may otherwise have under this Agreement with respect to defects other than year performance.

- PARTICIPATION:

Bidder may agree to extend the terms of the resulting contract to other political subdivision, municipalities and tax-supported agencies.

Such participating Governmental bodies shall make purchases in their own name, make payment directly to bidder, and be liable directly to the bidder, holding the County of Fresno harmless.

- CONFIDENTIALITY:

All services performed by vendor shall be in strict conformance with all applicable Federal, State of California and/or local laws and regulations relating to confidentiality, including but not limited to, California Civil Code, California Welfare and Institutions Code, Health and Safety Code, California Code of Regulations, Code of Federal Regulations.

Vendor shall submit to County’s monitoring of said compliance.

Vendor may be a business associate of County, as that term is defined in the “Privacy Rule” enacted by the Health Insurance Portability and Accountability Act of 1996 (HIPAA). As a HIPAA Business Associate, vendor may use or disclose protected health information (“PHI”) to perform functions, activities or services for or on behalf of County as specified by the County, provided that such use or disclosure shall not violate HIPAA and its implementing regulations. The uses and disclosures if PHI may not be more expansive than those applicable to County, as the “Covered Entity” under HIPAA’s Privacy Rule, except as authorized for management, administrative or legal responsibilities of the Business Associate.

Vendor shall not use or further disclose PHI other than as permitted or required by the County, or as required by law without written notice to the County.

Vendor shall ensure that any agent, including any subcontractor, to which vendor provides PHI received from, or created or received by the vendor on behalf of County, shall comply with the same restrictions and conditions with respect to such information.

- APPEALS:

Appeals must be submitted in writing within seven (7) working days after notification of proposed recommendations for award. A “Notice of Award” is not an indication of County’s acceptance of an offer made in response to this RFP/RFQ. Appeals should be submitted to County of Fresno Purchasing, 4525 E. Hamilton Avenue, Fresno, California 93702-4599. Appeals should address only areas regarding RFP contradictions, procurement errors, quotation rating discrepancies, legality of procurement context, conflict of interest, and inappropriate or unfair competitive procurement grievance regarding the RFP/RFQ process.

Purchasing will provide a written response to the complainant within seven (7) working days unless the complainant is notified more time is required.

If the protesting bidder is not satisfied with the decision of Purchasing, he/she shall have the right to appeal to the Purchasing Agent/CAO within seven (7) business days after Purchasing’s notification; except if, notified to appeal directly to the Board of Supervisors at the scheduled date and time.

If the protesting bidder is not satisfied with Purchasing Agent/CAO’s decision, the final appeal is with the Board of Supervisors.

- OBLIGATIONS OF CONTRACTOR:

  - CONTRACTOR shall perform as required by the ensuing contract. CONTRACTOR also warrants on behalf of itself and all subcontractors engaged for the performance of the ensuing contract that only persons authorized to work in the United States pursuant to the Immigration Reform and Control Act of 1986 and other applicable laws shall be employed in the performance of the work hereunder.

  - CONTRACTOR shall obey all Federal, State, local and special district laws, ordinances and regulations.

- AUDITS & RETENTION:

The Contractor shall maintain in good and legible condition all books, documents, papers, data files and other records related to its performance under this contract. Such records shall be complete and available to Fresno County, the State of California, the federal government or their duly authorized representatives for the purpose of audit, examination, or copying during the term of the contract and for a period of at least three (3) years following the County's final payment under the contract or until conclusion of any pending matter (e.g., litigation or audit), whichever is later. Such records must be retained in the manner described above until all pending matters are closed.

- DISCLOSURE – CRIMINAL HISTORY & CIVIL ACTIONS:

Applies to Request for Proposal (RFP); does not apply to Request for Quotation (RFQ) unless specifically stated elsewhere in the RFQ document.

In their proposal, the bidder is required to disclose if any of the following conditions apply to them, their owners, officers, corporate managers and partners (hereinafter collectively referred to as “Bidder”):

- Within the three-year period preceding the proposal, they have been convicted of, or had a civil judgment rendered against them for:

  - fraud or a criminal offense in connection with obtaining, attempting to obtain, or performing a public (federal, state, or local) transaction or contract under a public transaction;

  - violation of a federal or state antitrust statute;

  - embezzlement, theft, forgery, bribery, falsification, or destruction of records; or

  - false statements or receipt of stolen property

Within a three-year period preceding their proposal, they have had a public transaction (federal, state, or local) terminated for cause or default.

- DATA SECURITY:

Individuals and/or agencies that enter into a contractual relationship with the COUNTY for the purpose of providing services must employ adequate controls and data security measures, both internally and externally to ensure and protect the confidential information and/or data provided to contractor by the COUNTY, preventing the potential loss, misappropriation or inadvertent access, viewing, use or disclosure of COUNTY data including sensitive or personal client information; abuse of COUNTY resources; and/or disruption to COUNTY operations.

Individuals and/or agencies may not connect to or use COUNTY networks/systems via personally owned mobile, wireless or handheld devices unless authorized by COUNTY for telecommuting purposes and provide a secure connection; up to date virus protection and mobile devices must have the remote wipe feature enabled.  Computers or computer peripherals including mobile storage devices may not be used (COUNTY or Contractor device) or brought in for use into the COUNTY’s system(s) without prior authorization from COUNTY’s Chief Information Officer and/or designee(s).

No storage of COUNTY’s private, confidential or sensitive data on any hard-disk drive, portable storage device or remote storage installation unless encrypted according to advance encryption standards (AES of 128 bit or higher).

The COUNTY will immediately be notified of any violations, breaches or potential breaches of security related to COUNTY’s confidential information, data and/or data processing equipment which stores or processes COUNTY data, internally or externally.

COUNTY shall provide oversight to Contractor’s response to all incidents arising from a possible breach of security related to COUNTY’s confidential client information.  Contractor will be responsible to issue any notification to affected individuals as required by law or as deemed necessary by COUNTY in its sole discretion.  Contractor will be responsible for all costs incurred as a result of providing the required notification.

- PURCHASING LOCATION & HOURS:

Fresno County Purchasing is located at 4525 E. Hamilton Avenue (second floor), Fresno, CA 93702.  Non-holiday hours of operation are Monday through Friday, 8:00 A.M. to 12:00 Noon and 1:00 P.M. to 5:00 P.M. PST; Purchasing is closed daily from 12:00 Noon to 1:00 P.M.  The following holiday office closure schedule is observed:

| January 1* |  | New Year's Day |
| --- | --- | --- |
| Third Monday in January |  | Martin Luther King, Jr.’s Birthday |
| Third Monday in February |  | Washington - Lincoln Day |
| March 31* |  | Cesar Chavez’ Birthday |
| Last Monday in May |  | Memorial Day |
| July 4* |  | Independence Day |
| First Monday in September |  | Labor Day |
| November 11* |  | Veteran's Day |
| Fourth Thursday in November |  | Thanksgiving Day |
| Friday following Thanksgiving |  |  |
| December 25* |  | Christmas |
| * When this date falls on a Saturday, the holiday is observed the preceding Friday. If the date falls on a Sunday, the holiday is observed the following Monday. |  |  |

BIDDING INSTRUCTIONS
CONTRACT SERVICES

The County of Fresno Purchasing on behalf of various County Departments is soliciting bids to establish an agreement under which the successful bidder will provide all labor, materials, equipment, etc. as necessary to provide scheduled maintenance and corrective maintenance for the Uninterruptible Power Supply (UPS) Systems and Battery Power Units as specified within this Request for Quotation.

LOCAL VENDOR PREFERENCE:  The Local Vendor Preference does not apply to this Request for Quotation.

DEFINITIONS:  The terms Bidder, Proposer, Contractor and Vendor are all used interchangeably and refer to that person, partnership, corporation, organization, agency, etc. which is offering the quotation and is identified on page one of this Request For Quotation (RFQ).

VENDOR CONFERENCE/ SITE INSPECTION: On February 23, 2011 at 10:00 a.m., a vendor's conference/site inspection will be held in which the scope of the project and quotation requirements will be explained. The meeting will start at the Main Detention Facility located at 1225 “M” Street, Fresno, Ca. (meet at the front entrance) and continue to the other sites listed in this RFQ. An addendum to the RFQ will be prepared and distributed to all bidders only if necessary to clarify substantive items raised during the vendors' conference.

Bidders are to contact Craig Nickel at County of Fresno Purchasing, (559) 456-7110, if they are planning to attend the conference.

INTERPRETATION OF RFQ: Vendors must make careful examination of the requirements, specifications and conditions expressed in the RFQ and fully inform themselves as to the quality and character of services required.  If any person planning to submit a quotation finds discrepancies in or omissions from the RFQ or has any doubt as to the true meaning or interpretation, correction thereof may be requested at the scheduled Vendor Conference (see above).  Any change in the RFQ will be made only by written addendum, duly issued by the County.  The County will not be responsible for any other explanations or interpretations.

Questions may be submitted subsequent to the Vendor Conference, subject to the following conditions:

- Such questions are submitted in writing to County Purchasing at least five (5) County business days prior to the Request for Quotation closing date. Questions must be directed to the attention of the buyer identified on page one.

- Such questions are submitted with the understanding that County can respond only to questions it considers material in nature.

Questions shall be delivered to County of Fresno Purchasing, 4525 E. Hamilton Avenue, Fresno, CA 93702 or faxed to (559) 456-7831. If faxing, the bidder must confirm receipt by phone ((559) 456-7110), within one-half (½) hour of transmission.

NOTE: The bidder is encouraged to submit all questions at the Vendor Conference. Time limitations can prevent a response to questions submitted after the conference.

AWARD:  Award will be made to the vendor(s) offering the services deemed to be to the best advantage of the County.  The County shall be the sole judge in making such determination. Award Notices are tentative: Acceptance of an offer made in response to this RFQ shall occur only upon execution of an agreement by both parties or issuance of a valid written Purchase Order by Fresno County Purchasing.

RIGHT TO REJECT BIDS:  The County reserves the right to reject any and all bids and to waive informalities or irregularities in bids.

ISSUING AGENT: This RFQ has been issued by County of Fresno, Purchasing. Purchasing shall be the vendor’s sole point of contact with regard to the RFQ, its content, and all issues concerning it.

AUTHORIZED CONTACT: All communication regarding this RFQ shall be directed to an authorized representative of County Purchasing. The specific buyer managing this RFQ is identified on the cover page, along with his or her telephone number, and he or she should be the primary point of contact for discussions or information pertaining to the RFQ. Contact with any other County representative, including elected officials, for the purpose of discussing this RFQ, it content, or any other issue concerning it, is prohibited unless authorized by Purchasing. Violation of this clause, by the vendor having unauthorized contact (verbally or in writing) with such other County representatives, may constitute grounds for rejection by Purchasing of the vendor’s quotation.

The above stated restriction on vendor contact with County representatives shall apply until the County has awarded a purchase order or contract to a vendor or vendors, except as follows. First, in the event that a vendor initiates a formal protest against the RFQ, such vendor may contact the appropriate individual, or individuals who are managing that protest as outlined in the County’s established protest procedures. All such contact must be in accordance with the sequence set forth under the protest procedures. Second, in the event a public hearing is scheduled before the Board of Supervisors to hear testimony prior to its approval of a purchase order or contract, any vendor may address the Board.

NUMBER OF COPIES:  Submit one (1) original and four (4) copies of your quotation no later than the quotation closing date and time as stated on the front of this document to County of Fresno Purchasing.  Each copy is to be identical to the original, include all supporting documentation (i.e. literature, brochures, reports, schedules etc.).  The cover page of each quotation is to be appropriately marked “Original” or “Copy”.

FIRM QUOTATION: All quotations shall remain firm for at least ninety (90) days.

TAXES:  The quoted amount must include all applicable taxes. If taxes are not specifically identified in the quotation it will be assumed that they are included in the total quoted.

SALES TAX: Fresno County pays California State Sales Tax in the amount of 8.975% regardless of vendor's place of doing business.

MINOR DEVIATIONS:  The County reserves the right to negotiate minor deviations from the prescribed terms, conditions and requirements with the selected vendor.

QUOTATION REJECTION: Failure to respond to all questions or not to supply the requested information could result in rejection of your quotation.

BIDDERS’ LIABILITIES:  County of Fresno will not be held liable for any cost incurred by vendors in responding to the RFQ.

PRICE RESPONSIBILITY:  The selected vendor will be required to assume full responsibility for all services and activities offered in the quotation, whether or not they are provided directly.  Further, the County of Fresno will consider the selected vendor to be the sole point of contact with regard to contractual matters, including payment of any and all charges resulting from the contract.  The contractor may not subcontract or transfer the contract, or any right or obligation arising out of the contract, without first having obtained the express written consent of the County.

CONFIDENTIALITY:  Bidders shall not disclose information about the County's business or business practices and safeguard confidential data which vendor staff may have access to in the course of system implementation.

NEWS RELEASE:  Vendors shall not issue any news releases or otherwise release information to any third party about this RFQ or the vendor's quotation without prior written approval from the County of Fresno.

BACKGROUND REVIEW: The County reserves the right to conduct a background inquiry of each proposer/bidder which may include collection of appropriate criminal history information, contractual and business associations and practices, employment histories and reputation in the business community. By submitting a quotation/bid to the County, the vendor consents to such an inquiry and agrees to make available to the County such books and records the County deems necessary to conduct the inquiry.

EXCEPTIONS: Identify with explanation, any terms, conditions, specifications or stipulations of the RFQ with which you CAN NOT or WILL NOT comply.

ADDENDA: In the event that it becomes necessary to revise any part of this RFQ, addenda will be provided to all agencies and organizations that receive the basic RFQ.

SUBCONTRACTORS: If a subcontractor is proposed, complete identification of the subcontractor and his tasks shall be provided. The primary contractor is not relieved of any responsibility by virtue of using a subcontractor.

CONFLICT OF INTEREST:  The County shall not contract with, and shall reject any bid or quotation submitted by the persons or entities specified below, unless the Board of Supervisors finds that special circumstances exist which justify the approval of such contract:

- Employees of the County or public agencies for which the Board of Supervisors is the governing body.

- Profit-making firms or businesses in which employees described in Subsection (1) serve as officers, principals, partners or major shareholders.

- Persons who, within the immediately preceding twelve (12) months, came within the provisions of Subsection (1), and who were employees in positions of substantial responsibility in the area of service to be performed by the contract, or participated in any way in developing the contract or its service specifications.

- Profit-making firms or businesses in which the former employees described in Subsection (3) serve as officers, principals, partners or major shareholders.

- No County employee whose position in the County enables him to influence the selection of a contractor for this RFQ, or any competing RFQ, and no spouse or economic dependent of such employee, shall be employees in any capacity by a bidder, or have any other direct or indirect financial interest in the selection of a contractor.

INVOICING:  All invoices are to be delivered in duplicate to the ordering department. Each invoice shall reference the purchase order or contract no. The contractor shall obtain the “invoice to” address when receiving the order.

PAYMENT:  County will make partial payments for all purchases made under the contract/purchase order and accumulated during the month.

CONTRACT TERM: It is County’s intent to contract with the successful bidder for a term of three (3) years with the option to renew for two (2) additional one (1) year periods.

PRICES:  Bidder agrees that prices quoted are maximum for the contract period, and in the event of a price decline such lower prices shall be extended to the County of Fresno.

INDEPENDENT CONTRACTOR: In performance of the work, duties, and obligations assumed by Contractor under any ensuing Agreement, it is mutually understood and agreed that CONTRACTOR, including any and all of Contractor’s officers, agents, and employees will at all times be acting and performing as an independent contractor, and shall act in an independent capacity and not as an officer, agent, servant, employee, joint venturer, partner, or associate of the COUNTY.  Furthermore, County shall have no right to control or supervise or direct the manner or method by which Contractor shall perform its work and function.  However, County shall retain the right to administer this Agreement so as to verify that Contractor is performing its obligations in accordance with the terms and conditions thereof.  Contractor and County shall comply with all applicable provisions of law and the rules and regulations, if any, of governmental authorities having jurisdiction over matters the subject thereof.

Because of its status as an independent contractor, Contractor shall have absolutely no right to employment rights and benefits available to County employees. Contractor shall be solely liable and responsible for providing to, or on behalf of, its employees all legally-required employee benefits.  In addition, Contractor shall be solely responsible and save County harmless from all matters relating to payment of Contractor's employees, including compliance with Social Security, withholding, and all other regulations governing such matters.  It is acknowledged that during the term of the Agreement, Contractor may be providing services to others unrelated to the County or to the Agreement.

HOLD HARMLESS CLAUSE:  Contractor agrees to indemnify, save, hold harmless and at County's request, defend the County, its officers, agents and employees, from any and all costs and expenses, damages, liabilities, claims and losses occurring or resulting to County in connection with the performance, or failure to perform, by Contractor, its officers, agents or employees under this Agreement and from any and all costs and expenses, damages, liabilities, claims and losses occurring or resulting to any person, firm or corporation who may be injured or damaged by the performance, or failure to perform, of Contractor, its officers, agents or employees under this Agreement.

INSURANCE:

Without limiting the COUNTY's right to obtain indemnification from CONTRACTOR or any third parties, CONTRACTOR, at its sole expense, shall maintain in full force and effect, the following insurance policies or a program of self-insurance, including but not limited to, an insurance pooling arrangement or Joint Powers Agreement (JPA) throughout the term of the Agreement:

- Commercial General Liability

Commercial General Liability Insurance with limits of not less than One Million Dollars ($1,000,000) per occurrence and an annual aggregate of Two Million Dollars ($2,000,000). This policy shall be issued on a per occurrence basis.   COUNTY may require specific coverages including completed operations, products liability, contractual liability, Explosion-Collapse-Underground, fire legal liability or any other liability insurance deemed necessary because of the nature of this contract.

- Automobile Liability

Comprehensive Automobile Liability Insurance with limits for bodily injury of not less than Two Hundred Fifty Thousand Dollars ($250,000.00) per person, Five Hundred Thousand Dollars ($500,000.00) per accident and for property damages of not less than Fifty Thousand Dollars ($50,000.00), or such coverage with a combined single limit of Five Hundred Thousand Dollars ($500,000.00).  Coverage should include owned and non-owned vehicles used in connection with this Agreement.

- Professional Liability

If CONTRACTOR employs licensed professional staff, (e.g., Ph.D., R.N., L.C.S.W., M.F.C.C.) in providing services, Professional Liability Insurance with limits of not less than One Million Dollars ($1,000,000.00) per occurrence, Three Million Dollars ($3,000,000.00) annual aggregate.

- Worker's Compensation

A policy of Worker's Compensation insurance as may be required by the California Labor Code.

CONTRACTOR shall obtain endorsements to the Commercial General Liability insurance naming the County of Fresno, its officers, agents, and employees, individually and collectively, as additional insured, but only insofar as the operations under this Agreement are concerned. Such coverage for additional insured shall apply as primary insurance and any other insurance, or self-insurance, maintained by COUNTY, its officers, agents and employees shall be excess only and not contributing with insurance provided under CONTRACTOR's policies herein.  This insurance shall not be cancelled or changed without a minimum of thirty (30) days advance written notice given to COUNTY.

Within thirty (30) days from the date CONTRACTOR executes this Agreement, CONTRACTOR shall provide certificates of insurance and endorsement as stated above for all of the foregoing policies, as required herein, to the County of Fresno, stating that such insurance coverage have been obtained and are in full force; that the County of Fresno, its officers, agents and employees will not be responsible for any premiums on the policies; that such Commercial General Liability insurance names the County of Fresno, its officers, agents and employees, individually and collectively, as additional insured, but only insofar as the operations under this Agreement are concerned; that such coverage for additional insured shall apply as primary insurance and any other insurance, or self-insurance, maintained by COUNTY, its officers, agents and employees, shall be excess only and not contributing with insurance provided under CONTRACTOR's policies herein; and that this insurance shall not be cancelled or changed without a minimum of thirty (30) days advance, written notice given to COUNTY.

In the event CONTRACTOR fails to keep in effect at all times insurance coverage as herein provided, the COUNTY may, in addition to other remedies it may have, suspend or terminate this Agreement upon the occurrence of such event.

All policies shall be with admitted insurers licensed to do business in the State of California.  Insurance purchased shall be purchased from companies possessing a current A.M. Best, Inc. rating of A FSC VII or better.

DISPUTE RESOLUTION:  The ensuing contract shall be governed by the laws of the state of California.

Any claim which cannot be amicably settled without court action will be litigated in the U. S. District Court for the Eastern District of California in Fresno, CA or in a state court for Fresno County.

TERMINATION:  The County reserves the right to terminate any resulting contract upon written notice.

DEFAULT: In case of default by the selected bidder, the County may procure the services from another source and may recover the loss occasioned thereby from any unpaid balance due the selected bidder, or by any other legal means available to the County.

ASSIGNMENTS:  The ensuing proposed contract will provide that the vendor may not assign any payment or portions of payments without prior written consent of the County of Fresno.

ASSURANCES:  Any contract awarded under this RFQ must be carried out in full compliance with The Civil Rights Act of 1964, The Americans With Disabilities Act of 1990, their subsequent amendments, and any and all other laws protecting the rights of individuals and agencies.  The County of Fresno has a zero tolerance for discrimination, implied or expressed, and wants to ensure that policy continues under this RFQ.  The contractor must also guarantee that services, or workmanship, provided will be performed in compliance with all applicable local, state, or federal laws and regulations pertinent to the types of services, or project, of the nature required under this RFQ.  In addition, the contractor may be required to provide evidence substantiating that their employees have the necessary skills and training to perform the required services or work.

AUDITS AND RETENTION: The Contractor shall maintain in good and legible condition all books, documents, papers, data files and other records related to its performance under this contract. Such records shall be complete and available to Fresno County, the State of California, the federal government or their duly authorized representatives for the purpose of audit, examination, or copying during the term of the contract and for a period of at least three years following the County's final payment under the contract or until conclusion of any pending matter (e.g., litigation or audit), whichever is later. Such records must be retained in the manner described above until all pending matters are closed.

VENDOR ASSISTANCE: Successful bidder shall furnish, at no cost to the County, a representative to assist County departments in determining their service requirements.

SPECIFICATIONS: No exceptions to or deviations from this specification will be considered unless each exception or deviation is specifically stated by the bidder, in the designated places. If no exceptions or deviations are shown the bidder will be required to furnish items exactly as specified herein. The burden of proof of compliance with this specification is the responsibility of the bidder.

GUARANTEE AGAINST DEFECTS: All items are to carry a full guarantee against defects in materials and workmanship and guarantee against breakage and other malfunctions when performing work for which they are designed.

MATERIALS TO BE NEW:  All materials shall be new and of merchantable grade, free from defect. No bid will be considered unless it is accompanied by a complete list of manufacturer's catalog numbers of the items, which the bidder proposes to furnish, together with full descriptive literature on all items so enumerated.  If item proposed differs from these specifications, bidder shall present specific explanation of functioning and structural characteristics for those details which differ from the specifications listed herein.

EXAMINATION OF SITE:  Where work is to be performed on County site, each bidder shall have examined the site of work before bidding and shall be responsible for having acquired full knowledge of the job and of all problems affecting it.  No variations or allowance from the contract sum will be made because of lack of such examination.

DAMAGE TO EXISTING WORK:  Damage to existing construction, equipment, planting, etc., by the contractor in the performance of his work shall be replaced or repaired and restored to original condition by the contractor.

CLEAN-UP:  The Contractor shall at all times keep the premises clean from accumulation of waste materials or rubbish caused by his employees or work and shall remove all resulting work debris from the job site.

COORDINATE WORK WITH OWNER: Successful bidder shall coordinate and schedule the work with the County so that any interruption to the normal business operations be kept to a minimum.

SUPERVISION:  The Contractor shall give efficient supervision to the work, using therein the skill and diligence for which he is remunerated in the contract price.  He shall carefully inspect the site and study and compare all drawings, specifications and other instructions, as ignorance of any phase of any of the features or conditions affecting the contract will not excuse him from carrying out its provisions to its full intent.

STANDARD OF PERFORMANCE:  All work shall be performed in a good and workmanlike manner.

BIDDER TO COMPLETE:

| Name of Insurance Carrier: |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Public Liability: |  |  |  | Expires: |  |
| Worker's Compensation: |  |  |  | Expires: |  |

Proof of maintenance of adequate insurance will be required before award is made to vendor.

WARRANTY:

State the warranty and/or guarantee provisions applicable to this equipment or attach warranty form with your bid.

State Purchase Order mailing address:

| Phone Number: |  |  |
| --- | --- | --- |
| Fax Number: |  |  |
| e-mail address: |  |  |

Vendor must complete and return with Request for Quotation.

| Firm: |  |
| --- | --- |

REFERENCE LIST

Provide a list of at least five (5) customers for whom you have recently provided similar products/services.  Be sure to include all requested information.

| Reference Name: |  |  |  |  |  |  |  | Contact: |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Address: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| City: |  |  |  |  |  |  |  |  | State: |  |  |  |  | Zip: |  |  |  |
| Phone No.: |  | ( |  |  | ) |  | Date: |  |  |  |  |  |  |  |  |  |  |
| Service Provided: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Reference Name: |  |  |  |  |  |  |  | Contact: |  |  |  |  |  |  |  |  |  |
| Address: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| City: |  |  |  |  |  |  |  |  |  | State: |  |  |  |  | Zip: |  |  |
| Phone No.: |  | ( |  |  | ) |  | Date: |  |  |  |  |  |  |  |  |  |  |
| Service Provided: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Reference Name: |  |  |  |  |  |  |  | Contact: |  |  |  |  |  |  |  |  |  |
| Address: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| City: |  |  |  |  |  |  |  |  | State: |  |  |  |  | Zip: |  |  |  |
| Phone No.: |  | ( |  |  | ) |  | Date: |  |  |  |  |  |  |  |  |  |  |
| Service Provided: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Reference Name: |  |  |  |  |  |  |  | Contact: |  |  |  |  |  |  |  |  |  |
| Address: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| City: |  |  |  |  |  |  |  |  |  | State: |  |  |  |  | Zip: |  |  |
| Phone No.: |  | ( |  |  | ) |  | Date: |  |  |  |  |  |  |  |  |  |  |
| Service Provided: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Reference Name: |  |  |  |  |  |  |  | Contact: |  |  |  |  |  |  |  |  |  |
| Address: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| City: |  |  |  |  |  |  |  |  | State: |  |  |  |  | Zip: |  |  |  |
| Phone No.: |  | ( |  |  | ) |  | Date: |  |  |  |  |  |  |  |  |  |  |
| Service Provided: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Failure to provide a list of at least five (5) customers may be cause for rejection of this RFQ.

- SCOPE OF WORK

INTRODUCTION:

The County of Fresno has in operation Uninterruptible Power Supply (UPS) and battery power units located in facilities throughout the County.  The intent of this RFQ is to identify vendor(s) for service, including emergency service, annual maintenance and corrective services to these systems on an ongoing basis.  The County’s delivery of service to the citizens and employees of the County is dependent upon the reliable operation of these systems.

OVERVIEW:

This Request for Quotation provides interested firms with the information required to prepare and submit to the County quotations for scheduled and corrective maintenance.  The bidders will be responsible for supplying information on their ability to perform these services in a reliable, practical, cost-effective manner, while maintaining the highest technical standards, regardless of the day or time.

The County has identified its needs for a maintenance program and the submitted quotation shall meet these requirements.

Any questions requiring interpretation of the true meaning of specifications shall be requested in writing by email countypurchasing@co.fresno.ca.us or by fax (559) 456-7831 to County of Fresno Purchasing.  The deadline for submitting requests for clarification is February 16, 2011 at 8:00 a.m.

COMPETENCE OF BIDDER:

The importance of maintaining the identified equipment in a safe and efficient operating condition at all times demands that service be performed by a company who has satisfactorily maintained equipment of similar grade to the degree specified herein.

In order to demonstrate that the bidder can properly fulfill all of the services and conditions of these specifications, Contractor shall furnish with his bid a written statement showing that he has:

- A current license to perform the work in conformance with the Provisions of the State Business and Professions Code.  License Number shall be set forth in all bids and contracts.

- Satisfactorily preformed other contracts of similar nature and magnitude, to include names, telephone numbers, and scope of work for such agreements.

- Adequate capital and satisfactory business standing as required by the work. Financial statements to be provided upon request.

- The requisite organization of skilled and experienced technicians thoroughly trained in the inspection, testing, maintenance and repair of fire/intrusion/duress system and device repair under his direct employment and supervision.  Including names, years of experience etc.

- The requisite organization of skilled and experienced technicians thoroughly trained in the inspection, testing, maintenance and repair of UPS/battery/Power Systems repair under his direct employment and supervision.  Including names, years of experience etc.

- The necessary facilities and plant, including parts inventory located within two-hundred (200) miles radius of the County sites involved.

- Toll free communication facilities on a 24 hour-per-day, 365 days-per-year basis so his staff can be reached and will respond as specified herein.

- All proprietary information and diagnostic tools necessary to properly maintain, troubleshoot and adjust the County’s systems.

- The equipment protected by the UPS systems identified herein is essential to the County’s ability to serve citizens of the County on a 24-hour per day seven day per week basis, therefore the successful bidder shall have the ability to respond to the specified worksite within two (2) hours after receiving emergency Level I notification regardless of the day or time.

GENERAL REQUIREMENTS:

- Provide all labor, materials, appliances, tools, transportation, and equipment required to complete scheduled system maintenance and corrective maintenance as required within the Scope of Work.

- All work shall be in full compliance with current rules and regulations of all applicable codes.  Nothing in this RFQ is to be construed to permit work not conforming to these codes.  Applicable codes and regulations include, but are not limited to, the following:

  - National Fire Protection Association - NFPA

  - Uniform Building Code (Latest Edition)

  - American Society of Mechanical Engineers - ASME

  - American Society for Testing and Materials - ASTM

  - National Electrical Code - NEC (Latest Edition)

  - National Electrical Manufacturer’s Association - NEMA

  - Title 24, Building Safety, C.C.R.

  - Occupational Safety and Health Act – OSHA

  - Underwriters Laboratory - UL

  - All Local Codes

DURATION OF CONTRACT

It is the County’s intent to contract with the successful bidder(s) for a term of three (3) years with the option to renew for two (2) additional one (1) year periods.  The County reserves the right to terminate contract by giving the contractor written notice.

COUNTY COORDINATOR - RIGHTS AND RESPONSIBILITIES

The term “County Coordinator” shall refer to the person or persons responsible in the supervision of any Contract resulting from this Request for Quotation (RFQ).

It will be the duty of the County Coordinator to supervise the work as it progresses as well as to inspect materials, which are used in the work.  The duty of inspectors acting under the County Coordinators shall not be only to report deviations from the specifications, but they shall have the power to stop the work pending a decision by the County. The inspector shall have no power to alter the specifications.  Advice or directions given to the Contractor by the inspector shall not be binding upon the County; neither shall it release the Contractor from his responsibilities as herein stated.

It will be the right of the County at any time to stop defective work or to stop the entire work by the Contractor if he is not complying with the specifications and terms of the contract entered into between the County of Fresno and the Contractor.

The County shall have the right to require the Contractor to remove at any time any employee of the Contractor who shall be employed on this job and who appears to be incompetent, who acts in a disorderly, unsafe or improper manner, or fails to follow established protocols, including County rules and regulations and such person shall not be put back to work on the job without written consent of the County.

The County without invalidating the Contract, may order extra work or make changes by altering, adding to or deducting from the work only by written Orders, initiated by the County and properly approved and authorized by County of Fresno Purchasing ,setting forth the amount of money to be added or deducted.

DELIVERY REQUIREMENTS:

Facility Services, ITSD and the Sheriff Department will be responsible for the administration of the work requested through this Request for Quotation (RFQ).

Coordination and communication with Facility Services, ITSD and the Sheriff Department will be essential to the successful completion of the work.  All facilities will remain in full normal operation for the duration of the agreement and any need for disruption of the services provided in these facilities shall be presented with the quotation.

Upon award the County shall issue a Notice to Proceed and identify his designee(s) therein.  Only those designated by the County will have authority to make determinations under the agreement.

Corrective maintenance and any system component or parts replacement shall be approved by County prior to the start of work and be so indicated in writing on the approved service form.

CONTROL OF WORK AND INSTRUCTIONS:

The contractor shall provide diligent supervision of the work to the satisfaction of the County.

Contractor shall confine storage of materials to such limits as may be directed by the County and shall not unreasonably encumber the premises with materials and equipment.  Contractor shall enforce any instructions of the County regarding signs, advertising, fire, danger signals, barricades, and smoking, and shall require all persons employed on the work to comply with all building regulations while on the premises.

SCHEDULING OF WORK:

All maintenance service shall be scheduled subject to the review and approval of the County.  The contractor(s) shall be required to provide yearly schedules of the work within thirty (30) days of contract execution and on or before January 1, of the subsequent years.  These schedules must be adhered to throughout the term of the agreement.

No work shall interfere with the operation of the existing facilities on or adjacent to the site.  Normal Facility hours are, Monday to Friday 0700 to 1630.Work may be scheduled outside of normal working hours as approved by the County.

Contractor shall provide for approval by the County within thirty (30) days of contract execution the “Contractor Report of Service Form”.  This form will be required to document services rendered.  The form at a minimum shall include, date of service, time of arrival/departure, printed name and signature of technician providing the service, building number, unit identification, type of service (preventative/corrective/extra services), corrective action taken, description of devices serviced, tested or repaired, parts utilization, status of service/repair, electrical readings, printed name and signature of County representative authorizing the work, completion of work County representative printed name and signature.

SAFEGUARDS:

The Contractor shall provide, in conformity with all local codes and ordinances and as may be required, lockouts, fences, guardrails, barricades, lights, danger signs, enclosures, etc. and maintain such safeguards until work is complete.

Any fire hazardous operation shall have proper fire extinguisher, furnished by the contractor, close by and the adjacent area shall be policed before starting or stopping work for the day.  The contractor shall be responsible for all costs incurred by the County as a result of damage caused by the contractors operations, including costs associated with false fire alarms caused by the contractor.

The contractor shall ensure that the health and welfare of occupants of the building will not be effected by noise and fumes produced by the work.  The County reserves the right to halt any work, at any time it adversely affects the building occupants.

Any asbestos removal shall be by the County.  If the contractor discovers asbestos, which has not been removed, the contractor shall immediately cease work in that area and promptly notify the County or County Coordinator.

MATERIALS & WORKMANSHIP:

Materials and equipment shall be new unless otherwise approved by the County. Materials and equipment of a given type shall be of the same manufacture.  Materials and equipment shall be free of dents, scratches, marks, shipping tags, and all defacing features.

All material, equipment, devices, etc. shall be installed in accordance with the recommendations of the manufacture of the particular item.  The Contractor shall be responsible for all installations contrary to the manufacture’s recommendations.  The contractor shall make all necessary changes and revisions necessary for compliance.  Manufacturer’s installation instructions shall be delivered to and maintained on the jobsite through the duration of the project.

Any work which is done as an addition, expansion or remodel to an existing system or system component shall be compatible with that system and be approved prior to the installation.

Workmanship shall be to the best of trade practices, preformed by workers thoroughly trained and familiar with the respective systems.  The Contractor at the Contractor expense shall correct all defective workmanship.

The Contractor shall thoroughly clean all of his work, removing all debris, stain and marks resulting from his work.  This includes but is not limited to building surfaces, piping, and equipment. Surfaces shall be free of dirt, grease, labels, tags, tape, rust, and all foreign material.

Contractor shall ensure that before testing or servicing the systems notification is given to the appropriate County representative(s).  Contractor shall be responsible for all costs associated with system shutdowns, alarms or signals that result in interruption of business or unplanned evacuation.

Wiring in panel boards, and cabinets shall be neatly installed.  Wiring shall be grouped, laced, or clipped and fanned out to wiring terminals.

Wiring in all cabinets, panel boards, control panels shall be identified and clearly marked at termination.

Installation of conduit, junction boxes, and associated equipment shall be done in a neat manner secured to the structure or suspended on conduit hangers.

All wiring and construction prints or diagrams of systems covered under this contract are the property of the County and upon termination of this contract shall be delivered to the County.  Absolutely no changes are to be made to the circuitry or mechanical systems without prior approval of the County.  Any changes without prior approval may be considered a breach of contract.  All changes in circuitry made by Contractor shall be properly recorded on the diagrams, including date of change and name of person making same.  It is the responsibility of the Contractor to maintain clean, legible, readable and accurate schematics and wiring diagrams at all times.  Prints and diagrams are to remain on the job site.

RESPONSIBILITY OF CONTRACTOR:

Contractor shall take responsibility for the work, and shall bear all losses resulting to him on account of the negligence of the Contractor.  Contractor shall be responsible for all work of subcontractors and shall assume the defense of and indemnify and save harmless the County of Fresno and any of its officers and their agents from claims of any kind arising from the negligent performance of this Contract by the Contractor or any of his subcontractors.  Contractor shall not be liable for injuries or damage to persons or property except those directly due to his own acts or omissions, and the responsibility of the County for injuries or damage to persons or property while on or about the equipment being maintained hereunder is in no way affected by this Agreement.  Contractor shall not be liable for any loss, damage or delay caused by strikes, lock-outs, fire, theft, floods, riot, civil commotion, war, malicious mischief, act of God or any cause beyond his reasonable control.

No equipment-requiring repair shall be allowed to remain out of service due to the lack of diligent effort by the Contractor.  Any part or equipment locally available will be purchased locally if necessary to expedite the job.  Repairs shall be begun and carried to completion as soon as possible unless the County approves other arrangements.

Contractor shall in no case allow the performance of work by subcontract unless the subcontractor has been approved by the County, and in no case shall the use of subcontractors in any way alter the position of the Contractor or his sureties with relation to his Contract with Fresno County.  When a subcontractor is used the responsibility for every portion of the work shall still remain with the Contractor.

Contractor shall obtain prior approval of the County in writing for any area or space required for the Contractor’s storage during operations. This space will be maintained in a clean and orderly fashion.

Materials, equipment, etc. shall not be piled or stored in any location, which shall interfere with the conduct of the normal functions of the building or property.  All required safety precautions such as barricades, signs, danger signals, etc., shall be furnished and installed by the Contractor during operations.

Upon demand of the County, the Contractor shall correct any dangerous or hazardous situations that the County may indicate.

Contractor shall completely protect against damage from either materials or equipment all surfaces, equipment and facilities, adjoining his work, including, but not limited to woodwork, wall and floors.  All repair or replacement costs resulting from this damage shall be borne by the Contractor.  At the conclusion of each day’s work, the Contractor shall remove refuse, debris or waste materials and leave the premises in an orderly condition as required by the County.

Contractor must specify the degree of support the County may be required to furnish to accomplish the requirements of this agreement, if any.  Specify the man-hours required, and the nature of County’s participation within the scope of the agreement.

Contractor shall provide sufficient technicians for the service of the systems listed in this agreement in accordance with the specifications herein. Technicians utilized for UPS and battery maintenance shall be qualified and experienced in the inspection, testing, and maintenance of these systems. Contractor may be required at any time to provide substantiation and verification of qualifications of their employee(s) upon request of the County

Contractor shall provide, for approval by the County, the procedure to be followed for requesting services provided in this agreement.  This procedure will include, method of requesting service, ability to provide estimated arrival time of technician to site, reporting of call completion, communication with requesting staff and technician servicing the contract, etc.

EXTRA WORK - CHANGE IN WORK:

The County, without invalidating the Contract, may order extra work or make changes by altering, adding to or deducting from the work only by written Orders, initiated by the County and properly approved and authorized  by the County of Fresno Purchasing ,setting forth the amount of money to be added or deducted.

SPECIAL CONDITIONS:

In the event that the County will withdraw any equipment from service, or the usefulness of any equipment shall end, during the term of this Contract, the Contractor shall agree to negotiate an acceptable reduction of cost for services for the balance of the duration of said Contract.

The successful bidder shall have verifiable experience in a detention facility environment and be regularly engaged in the service and repair of UPS AND battery systems.

MANNER AND TIME OF CONDUCTING THE WORK:

All work shall be performed by skilled technicians and helpers directly employed and supervised by the Contractor.  Only qualified system technicians with a minimum of 4 years journeyman experience or manufacturer’s certification shall be allowed to perform service or maintenance work.  Helpers must work under the direct supervision of a journeyman technician.

Except for emergency callback service and minor repairs and/or adjustments hereinafter provided for, all work shall be performed during regular working hours and days.  Regular working hours are from 7:00 a.m. until 6:00 p.m. Monday through Friday.  County holidays excluded.

All equipment shutdowns for regular maintenance or extra examinations shall be scheduled in advance with the designated County representative and approved by the County so as not to interfere with building operations during the peak usage times.  Shutdowns in excess of one hour may require scheduling outside of normal business hours.  No extra charges will be incurred because of a scheduled shutdown regardless of day or time.

EMERGENCY WORK:

All work of a callback nature or trouble calls shall be treated as an emergency and work commenced shall be carried through to completion without delay.

Provide 24-hour emergency callback service for all equipment maintained hereunder.  Emergency callback service shall consist of prompt response to requests from the County or his authorized representatives for emergency services on any day of the week, at any hour of the day or night.  An emergency callback is defined as any necessity for maintenance, minor repair and/or adjustment of equipment between regular service calls to restore normal equipment operation.  Emergency callbacks will be categorized as follows:

LEVEL I - Requires onsite response in two (2) hours or less.

LEVEL II - Requires onsite response in eight (8) hours or less.

LEVEL III- Requires onsite response at 0800 hours, the next day

Due to the criticality of the protected systems, 911 Dispatch, Detention Door Controls, and Countywide Information Systems, determination of call level is at the discretion of the County or his authorized representative.  Failure to furnish emergency callback service within the above-specified time of notification of need may result in termination of the contract, withholding of payment, and/or another contractor to be hired to complete the work at the current contractor’s expense.

MINIMUM REQUIREMENTS FOR SITE VISITS:

- FRESNO COUNTY DETENTION FACILITY:

- 3 EACH LIEBERT 50 KVA, MODEL UDA63050A25RT04 (AP356) Serial No. M16460F,P32821 & P32822, 480V 3ph in 480V 3ph out, with 30 Johnson Control 12-270/each or equivalent. (Note: Located in Bldg. 608 roof room & 2 ea in basement)

- 1 EACH LIEBERT 40 KVA, Model UDA63040C25RT04 (AP346) Serial No. P32413, 480V 30ph in 208V 30ph out, w/ 30 Johnson Control 12-270FR or equivalent. (Note: Located in Bldg. 608)

- 1 EACH MITSUBISHI 50 KVA Model UP2033C-B503SU-2. (Note: Located in Bldg. 607, 1st floor Elec. Rm.)

- 1 EACH MITSUBISHI 40 KVA Model UP2033C-B403SU-2. (Note: Located in Bldg. 607, 2nd floor Elec. Rm.)

- 1 EACH MITSUBISHI 20 KVA, Model up2033c-b1535v-2, Serial #02-663j0102, with 30 (internal) Yuasa NP-18-12B or equivalent. (Note: Located in Bldg. 605, Laundry Storage; for Violent Offender Control)

- 1 EACH LIEBERT Model N Power, Serial No. M08F30007, Part No. 37SA03AAC6EH 76 (Note: Located in Bldg. 701, Room E112)

- 1 EACH LIEBERT Model N Power, Serial No. M08F30006, Part No. 37SA03AAC6EH 76 (Note: Located in Bldg. 701, Room B-245)

PROVIDE ONE SCHEDULED MAINTENANCE VISIT PER YEAR FOR EACH UPS.

PROVIDE ONE SCHEDULED MAINTENANCE VISIT PER YEAR FOR BATTERIES.

(DOES NOT INCLUDE CORRECTIVE MAINTENANCE AND PARTS.)

- FRESNO COUNTY SHERIFF ADMINISTRATION BUILDING:

- Liebert AP 341 30 KVA, Batteries (Sealed), 30 Each PRC-1290S

PROVIDE TWO SCHEDULED MAINTENANCE VISITS PER YEAR FOR EACH UPS. (Corrective maintenance parts not included/labor included.)

PROVIDE FOUR SCHEDULED MAINTENANCE VISITS PER YEAR FOR BATTERIES AND CHARGING SYSTEM. (Corrective maintenance parts and labor included.)

- FRESNO COUNTY ITSD, PLAZA BUILDING, 1020 S. TENTH STREET,
UMC HOSPITAL:

- Toshiba 50 KVA, Battery (Sealed), 30 each Datasafe 12HX330FR

- Toshiba 225 KVA, Battery (Sealed), 80 each CSB XHRL12620WFR

- Toshiba 225 KVA, Battery (Sealed), 80 each CSB XHRL12620WFR

- MGE 36 KVA, Battery (Sealed) 20 each Datasafe NPX 150RFR

PROVIDE TWO SCHEDULED MAINTENANCE VISITS PER YEAR FOR EACH UPS. (Includes corrective maintenance parts replacement.)

PROVIDE FOUR SCHEDULED MAINTENANCE VISITS PER YEAR FOR BATTERIES AND CHARGING SYSTEM. (Corrective maintenance parts and labor included.)

MAINTENANCE REQUIREMENTS:

SCHEDULED UPS MAINTENANCE VISITS SHALL, AT A MINIMUM, INCLUDE THE FOLLOWING IF APPROPRIATE TO EQUIPMENT:

- Comply with all site safety and security requirements.

- Perform and record maintenance per OEM specifications

- Clean cabinet and surrounding operational area.

- Check internal / external airflow and all fans.

- Measure and record ambient / operating noise levels.

- Perform IR scan for normal heat signature.

- Check for excessive mechanical / magnetic vibrations.

- Record Key components and ambient operating temps.

- Inspect all components for abnormalities.

- Check and correct all connections to proper torque rating.

- Record normal operation conditions and parameters.

- Record solid state filter assemblies currents

- Record capacitor filter assemblies voltage / current.

- Record magnetic filter assemblies voltage / current.

- Check and adjust display meters and indicators.

- Record input/output neutral and ground readings.

- Perform Sub-Systems periodic tests.

- Calibrate sub-systems.

- Check all circuit breakers and fuses.

- Check remote input/output displays/interfaces.

- Check operating environment safeties.

- Check for applicable seismic compliance requirements.

- Identify in writing all discrepancies and deficiency.

- Provide written report of service.

- Review report with facilities personnel.

SCHEDULED BATTERY MAINTENANCE VISITS SHALL, AT A MINIMUM, INCLUDE THE FOLLOWING:

- Comply with all site Safety and security requirements.

- Perform and record maintenance per OEM specifications.

- Clean racks and cabinets.

- Correct all rack and cabinet connector hardware deficiency.

- Check internal / external airflow and fans.

- Record piolet cell/jar ambient operating temps.

- Inspect all components for abnormalities.

- Perform IR scan for normal operating heat signatures.

- Inspect all jars for cracks, leaks, swelling, etc.

- Remove/correct all terminal / connector corrosion.

- Check and correct all connections to proper toque rating.

- Correct all terminal deficiencies.

- Inspect and correct for proper terminal coating.

- Record normal operating conditions and parameters.

- Record all cell / jar float voltages.

- Record ground voltage and current.

- Record all cell / jar impedance voltages.

- Record all charger filter assemblies voltages and currents.

- Record charger float and ripple voltages and currents.

- Adjust charger to temperature-compensated float voltage.

- Check LVSD.

- Check all circuit breakers and fuses.

- Perform normal load test (vice resistive load test).

- Profile / estimate minimum back-up time.

- Check remote input/output displays / interfaces.

- Check for seismic compliance.

- Identify in writing all discrepancies or deficiency.

- Provide written service report and review with facility personnel.

NON-SEALED SYSTEMS ALSO INCLUDE:

- Inspect jar hardware (flame arrestors, vents, caps, etc.)

- Identify & record critical sediment levels.

- Record electrolyte specific gravity, temperature, and level.

- Inspect internal components (plates, separators, etc.).

- Check inter-cell / jar connector impedance.

- Correct electrolyte level with distilled water.

- Proper release of hydrogen gas bubbles.

SECURITY REQUIREMENTS
DETENTION FACILITY

SECURITY:  The County of Fresno Jail is a no hostage facility (see Attachment “A”) operated by the County Sheriff’s Department.

The security of the Detention Facility is paramount and takes precedence over all construction processes.  Before the start of any work, the Contractor and any subcontractors shall review with a representative of the Sheriff’s Department and County Coordinator, the proposed construction process and how his work will interface with the Detention Facility operations.  The Detention Facility operations shall take precedence.  Contractor shall perform his work in accordance with the procedures established by the Sheriff’s Department.  Should any revisions to any procedures become necessary, such revisions shall be reviewed and approved by the Sheriff’s Department and the County Coordinator before execution of such revisions.  Exit facilities, distress warning devices and similar devices and equipment shall remain operable at all times in accordance with regulations of the State Fire Marshall.

The Contractor shall plan and execute his work in such a manner so as to prevent a breach of the Detention Facility Security.  This maintenance of security shall remain in effect for the duration of the project.

The Contractor shall be responsible for preventing the introduction of any material or equipment into the facility that could be deemed contraband.  Such contraband shall include, but not be limited to, tools, equipment, supplies, construction waste and construction materials.

Only tools, supplies and equipment necessary to complete a given task shall be taken into an inmate occupied space.  Such tools, supplies and materials shall be inventoried in and out of the secured area by the Contractor.  Any discrepancy shall immediately be called to the attention of the Sheriff’s Department.

The Sheriff’s Department may limit the number of workmen in any one area at one time.  Only workmen with proper identification as issued by the Sheriff’s Department shall be allowed into the work area within the Detention Facility.  The appropriate identification will be issued individually on an as needed basis.

On a daily basis and only for the work area involved, the Sheriff’s Department will issue the authorized representative of the Contractor one set of keys for access to the work area.  Keys shall be returned to the Sheriff’s Department at the end of each work day.  Should the Contractor lose any keys, he shall be responsible for the cost of replacement of key, lockset or keyway.  Loss of any key shall be reported immediately to Sheriff’s Department and County Coordinator.

Detention Facility has no “off hours”.  The contractor shall confer with Sheriff’s Department representative and County Coordinator on a case-by-case basis for all work to be performed outside of normal hours.

Any violations of security procedures by the Contractor which result in extraordinary man hour expenditures by the County, such as for unscheduled searches to retrieve construction contraband or man hour costs expended to report and/or recapture an escapee will be the responsibility of the Contractor.

Attachment “A”

PURPOSE:

The purpose of this policy is to establish procedures which provide for the resolution of a hostage-taking incident while preserving the safety of staff, public, inmates, and hostages, and maintaining facility security.

POLICY:

The Fresno County Sheriff's Office Jail Division maintains a NO HOSTAGE FACILITY and will not consider bargaining with hostage takers for ANY reason.

It is the policy of the Fresno County Sheriff's Office Jail Division that once any staff member is taken hostage, they immediately lose their authority and any orders issued by that person will not be followed regardless of their rank or status.

It is the policy of the Fresno County Sheriff's Office Jail Division that the primary responsibility of all staff members in a hostage situation is to protect every person involved, if possible, from serious injury or death.

PROCEDURES:

- DEFINITION

Hostage Situation:   any staff member, citizen or inmate held against their will by another person for the purpose of escape, monetary gain or any reason which may place an individual in danger of losing life or suffering serious injury.

- NOTIFICATIONS, CONTAINMENT AND CONTROL OF THE SITUATION

- Emergency procedures and notifications shall be implemented as per Emergency Planning procedures (B-101/FILE: EMERGENCY).

- The Watch Commander will notify the Patrol Watch Commander and apprise them of the incident.  The Patrol Watch Commander may be requested to activate the Crisis Negotiations Team (CNT), outside support agencies, equipment, personnel, and dispatch a detective to the scene for the crime report.

- DURING NEGOTIATIONS

  - While at the scene, the CNT members will conduct all verbal or written communications between the hostage taker(s) and the Incident Commander.  CNT will immediately notify the Incident Commander of any changes in the following situations:

    - Hostage status

    - Incident changes and developments

    - Hostage taker demands

    - Any and all pertinent information concerning the incident

  - Staff members at the scene not actively involved with negotiations will not act or speak out to the hostage taker(s) or hostages.

  - The Tactical Commander will formulate a plan to take the necessary actions, using the appropriate force, to terminate the hostage situation in the event negotiations fail.  Hostage safety will be of paramount concern.

- HOSTAGE SURVIVAL STRATEGIES[SRC1]

  - If taken hostage, it is important to make the transition from being a victim to being a survivor.  The following are not strict rules that must be rigidly followed, but rather general guidelines.  There will always be exceptions.

    - Regain/maintain composure.  Try to be calm, focused and clear-headed at all times.  Do not stand out from other hostages.  Drawing unnecessary attention increases the chance of being singled out and victimized.

    - Maintain a low-key, unprovocative posture.  Overt resistance is usually counterproductive in a hostage situation.

      - Remain calm and follow instructions.  Comply with the hostage takers when at all possible.

      - Be stoic.  Maintain an outward face of acceptance of adversity with dignity.  Avoid open displays of cowardice and fear.  Inmates will view frailty and feebleness as weakness, which may lead to victimization.

      - Do not antagonize, threaten or aggravate the hostage takers.  Avoid saying “no”, or arguing with the hostage takers.  Do not act authoritative.  The hostage takers must make it known that they are in charge.

      - Eye contact may be regarded as a challenge; make eye contact with the hostage takers sparingly.

      - Fight off basic instincts, such as anger and hostility. Be polite and remain alert.  Speak normally and don’t complain.

    - Hostages should try to establish a level of rapport or communication with their captors in attempt to get the captors to recognize them as human beings.

      - Find a mutual ground, an association with the hostage takers.  Foster communication on non-threatening topics (e.g., family, hobbies, sports, interests).

      - Use the captors’ first names, if known.  However, if hostage takers are attempting to conceal their identity, do not give any indication that they are recognized.

      - Listen actively to the captors’ feelings and concerns, but never praise, participate in, or debate their "cause”.  If they want to talk about their cause, act interested in their viewpoints.  Avoid being overly solicitous, which may be viewed as patronizing or insincere.

      - Do not befriend the inmates; such an attempt will likely result in exploitation.

      - Try asking for items that will increase personal comfort.  Make requests in a reasonable, low-key manner.

    - Be prepared to be isolated and disoriented.

      - Do not talk to other hostages.  The hostage takers may think a plot is being formed.

      - Develop mind games to stimulate thinking and maintain mental alertness.

    - Be tolerant of fellow hostages.  Just as each person has different reactions to stress, each individual will have different methods of coping as a hostage.  Some methods are not effective and may endanger the group, or be annoying to other hostages (e.g., constant talking).  Try to help these people cope in other ways.

    - Gather intelligence.  Hostages should take in and store as much detail, about their captors as possible without drawing attention to their efforts.  Make mental notes and attempt to gather the following information:  identification of the ring leader, the number of hostage takers, the type of weapons they are using, their tactics, location within the area, etc.

    - Maintain hope.  Depending on the circumstances, resolution of hostage situations can be a lengthy process.

  - Stay away from doors and windows through which rescue teams may enter or shoot.  If a rescue is attempted, drop to the floor and keep hands in view.

  - If there is a chance to escape, the hostage should be certain of their success.

    - Balance the likely payoff of any behavior with the possible consequences.  Hostage takers may use violence or death to teach a lesson.

    - Realize that Central Control will not open any doors for anyone.

  - Hostages should be aware of the “Stockholm Syndrome”, whereby hostages begin to show sympathy toward their captors.  Hostages who develop Stockholm Syndrome often view the captor as giving life by simply not taking it.  Such hostages often misinterpret a lack of abuse as kindness and may develop feelings of appreciation for the perceived benevolence. [SRC2]

PROGRAM DESCRIPTIONS

UPS Programs

| Standard | 2 scheduled maintenance visits per year (Corrective maintenance parts not included) Includes Full Battery program |
| --- | --- |
| Full | 2 scheduled maintenance visits per year (Includes corrective maintenance parts) Includes Full Battery program |
| Plus | 1 Scheduled maintenance visit per year (Corrective maintenance parts/labor not included) Includes Plus Battery program |

Battery Programs

| Full | 4 scheduled maintenance visits per year Locates batteries indicating imminent failure Includes failed battery replacement at the rate of 10%/year up to “end of life” Designed for battery systems eligible for the manufacturer’s full warranty period |
| --- | --- |
| Plus | 2 scheduled maintenance visits/year (Corrective maintenance parts and labor not included) |

(Apply only where indicated in Quotation Schedule)

| QUOTATION SCHEDULE |  |  |  |
| --- | --- | --- | --- |
| - DETENTION FACILITY |  |  |  |
| Note: Vendor to provide the Annual cost per unit for the services specified. |  |  |  |
| DESCRIPTION | QTY | ANNUAL COST PER UNIT |  |
| LIEBERT 50 KVA, MODEL UDA63050A25RT04 (AP356) Serial No. M16460F,P32821 & P32822, 480V 3ph in 480V 3ph out, with 30 Johnson Control 12-270/each or equivalent. (Note: Located in Bldg. 608 roof room & 2 ea in basement) | 3 | $ | each |
| LIEBERT 40 KVA, Model UDA63040C25RT04 (AP346) Serial No. P32413, 480V 30ph in 208V 30ph out, w/ 30 Johnson Control 12-270FR or equivalent. (Note: Located in Bldg. 608) | 1 | $ | each |
| MITSUBISHI 50 KVA Model UP2033C-B503SU-2. (Note: Located in Bldg. 607, 1st floor Elec. Rm.) | 1 | $ | each |
| MITSUBISHI 40 KVA Model UP2033C-B403SU-2. (Note: Located in Bldg. 607, 2nd floor Elec. Rm.) | 1 | $ | each |
| MITSUBISHI 20 KVA, Model up2033c-b1535v-2, Serial #02-663j0102, with 30 (internal) Yuasa NP-18-12B or equivalent. (Note: Located in Bldg. 605, Laundry Storage; for Violent Offender Control) | 1 | $ | each |
| LIEBERT Model N Power, Serial No. M08F30007, Part No. 37SA03AAC6EH 76 (Note: Located in Bldg. 701, Room E112) | 1 | $ | each |
| LIEBERT Model N Power, Serial No. M08F30006, Part No. 37SA03AAC6EH 76 (Note: Located in Bldg. 701, Room B-245) | 1 | $ | each |
| *PROVIDE ONE SCHEDULED MAINTENANCE VISIT PER YEAR FOR EACH UPS. |  |  |  |
| *PROVIDE ONE SCHEDULED MAINTENANCE VISIT PER YEAR FOR BATTERIES. |  |  |  |
| *(DOES NOT INCLUDE CORRECTIVE MAINTENANCE AND PARTS.) |  |  |  |

| QUOTATION SCHEDULE |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | LOCATION | MAINTENANCE PROGRAM |  |  | BATTERY REPL | ANNUAL COST |  |
| - SHERIFF |  |  |  |  |  | $ |  |
| Liebert AP341 30KVA |  | Standard |  |  |  |  |  |
| Batteries (Sealed) 30 each PRC-1290S |  | Full |  |  | Y |  |  |
| PROVIDE TWO SCHEDULED MAINTENANCE VISITS PER YEAR FOR EACH UPS. (Corrective maintenance parts not included/labor included.) |  |  |  |  |  |  |  |
| PROVIDE FOUR SCHEDULED MAINTENANCE VISITS PER YEAR FOR BATTERIES AND CHARGING SYSTEM. (Corrective maintenance parts and labor included.) |  |  |  |  |  |  |  |
| - ITSD |  |  |  |  |  |  |  |
| Plaza Building 21st Floor |  | Standard |  |  |  | $ |  |
| Toshiba 50 KVA Model T42D3F500XAMXN (4200FA XT) 30 each Battery (Sealed) Datasafe 12HX330FR |  | Full |  |  | Y |  |  |
| 10th Street – Unit 1 |  | Standard |  |  |  | $ |  |
| UPS1 Toshiba 225 KVA Model T90S3S22KS6XSN 80 each Battery (Sealed) CSB XHRL12620WFR |  | Full |  |  | Y |  |  |
| 10th Street – Unit 2 |  | Standard |  |  |  | $ |  |
| UPS1 Toshiba 225 KVA Model T90S3S22KS6XSN 80 each Battery (Sealed) CSB XHRL12620WFR |  | Full |  |  | Y |  |  |
| UMC Hospital Computer Room |  | Standard |  |  |  | $ |  |
| MGE 36 KVA Model 72-160030-00 (EPS-3036/42,66) 20 each Battery (Sealed) Datasafe NPX 150 RFR |  | Full |  |  | Y |  |  |
| PROVIDE TWO SCHEDULED MAINTENANCE VISITS PER YEAR FOR EACH UPS. (Includes corrective maintenance parts replacement.) |  |  |  |  |  |  |  |
| PROVIDE FOUR SCHEDULED MAINTENANCE VISITS PER YEAR FOR BATTERIES AND CHARGING SYSTEM. (Corrective maintenance parts and labor included.) |  |  |  |  |  |  |  |
| QUOTATION SCHEDULE CORRECTIVE MAINTENANCE LABOR AND MATERIALS RATES |  |  |  |  |  |  |  |
| ON SITE LABOR RATES: |  |  |  |  |  |  |  |
| NORMAL HOURS |  |  |  | $ |  |  | HOUR |
| (Monday – Sunday 0700-2300) |  |  |  |  |  |  |  |
| AFTER NORMAL HOURS |  |  |  | $ |  |  | HOUR |
| HOLIDAY HOURS |  |  |  | $ |  |  | HOUR |
| PORTAL TO PORTAL RATES: |  |  |  |  |  |  |  |
| NORMAL HOURS |  |  |  | $ |  |  | HOUR |
| AFTER NORMAL HOURS |  |  |  | $ |  |  | HOUR |
| HOLIDAY HOURS |  |  |  | $ |  |  | HOUR |
| TRAVEL/MILEAGE: |  |  |  |  |  |  | PER MILE |
| MILEAGE |  |  |  | $ |  |  |  |
| DAILY PER DIEM |  |  |  | $ |  |  | PER DAY |
| OTHER (Indicate how charges are calculated) |  |  |  | $ |  |  |  |
| (Lodging, Air Fare, etc.) |  |  |  |  |  |  |  |
| MATERIALS: |  |  |  |  |  |  |  |
| Provide a price sheet of major component and replacement batteries for systems indicated. |  |  |  |  |  |  |  |
| Other Material |  |  |  |  |  |  |  |
| Cost Plus |  |  |  |  |  |  | % |
| Serviceman’s name, address and phone number during: |  |  |  |  |  |  |  |
| - Regular working hours (8:00 a.m. to 5:00 p.m.) |  |  |  |  |  |  |  |
| - After regular working hours: |  |  |  |  |  |  |  |
| Other person/location, address or phone number where service/maintenance may be obtained: |  |  |  |  |  |  |  |
| Minimum Charge: (Explain in Detail): |  |  |  |  |  |  |  |

CHECK LIST

This Checklist is provided to assist the vendors in the preparation of their bid response.  Included in this list, are important requirements and is the responsibility of the bidder to submit with the bid package in order to make the bid compliant.  Because this checklist is just a guideline, the bidder must read and comply with the bid in its entirety.

Check off each of the following:

|  |  | The Request for Quotation (RFQ) has been signed and completed. |
| --- | --- | --- |
|  |  | One (1) original and two (2) copies of the RFQ have been provided. |
|  |  | Addenda, if any, have been completed, signed and included in the bid package. |
|  |  | The completed Reference List as provided with this RFQ. |
|  |  | The Quotation Schedule as provided with this RFQ has been completed, priced reviewed for accuracy and any corrections initialed in ink. |
|  |  | Indicate all of bidder exceptions to the County’s requirements, conditions and specifications as stated within this RFQ. |
|  |  | Bidder to Complete page as provided with this RFQ. |
|  |  | Lastly, on the LOWER LEFT HAND CORNER of the sealed envelope, box, etc. transmitting your bid include the following information: |

| County of Fresno RFQ No. |  |  | 285-4894 |
| --- | --- | --- | --- |
| Closing Date: | March 9, 2011 |  |  |
| Closing Time: | 2:00 P.M. |  |  |
| Commodity or Service: |  |  |  |

This Checklist does not need to be returned with your bid.