FIRE SUPPRESSION SYSTEM ROUTINE SERVICE AND MAINTENANCE CHECK LIST FOR HEAVY EQUIPMENT AT THE AMERICAN AVENUE DISPOSAL SITE

| NAME: |  | DATE: |  | CO. EQUIPMENT #: |  |
| --- | --- | --- | --- | --- | --- |

The following shall be performed during routine service and maintenance of the fire suppressions systems for the heavy equipment. A task list shall be completed for each equipment and submitted to the Disposal Site Supervisor or his designee, upon completion of services required.  All tasks listed shall be performed at a minimum and is not limited to the following:

Hook up squib simulator (check dates of squib or linear actuators).

Push the check circuit monitor button to test lights on the panel (if applicable).

Check that all wires and hoses in the cab are secure and not damaged.

Test inside actuator, manual or electrical, push to test and clean with WD40.

Remove inside cartridge, inspect, check gauge and clean with WD40.

Clean all the components in the cab and wipe down with WD40.

Remove manual or manual electrical actuator from the top of agent cylinders.

Clean the pneumatic actuator with WD40 and spray under the head to keep the metal locking spring from rusting.

Remove the distribution hose from the back of the bottle and clean the O-ring with WD40.

Inspect the head of the bottle-gauge guard, safe discs, and spring then clean with WD40.

Inspect the bottled cylinder for damage or rust (check bottle dates).

Inspect outside manual or electrical actuator, push to test and clean with WD40.

Remove outside cartridge, inspect, gauge and clean with WD40.

Inspect all 1/4 inch actuator hoses for proper mounting, damage or wear.

Pressure test all ¼ inch hoses with 500+ lbs of nitrogen from each manual actuator.

Inspect all check valves are in place and working properly.

Inspect all pneumatic actuators and vent checks function properly.

Inspect all ½ inch and ¾ inch hoses for proper mounting, damage, or wear.

Inspect all ½ inch and ¾ inch hoses with 500+ lbs of Nitrogen.

Inspect all nozzle covers are on, then blow the lines (note: don’t blow lines first and then install covers).

Inspect all nozzles are properly mounted.

Inspect all that all hoses are installed to factory specifications.

Inspect all wires are properly secured and not damaged.

Inspect all connections are secured and not damaged.

Test all linear fire wire with jumping a wire across the terminal in the end-of-line module.

Test each thermostat with heat, check for damage.

Inspect end-of-line modules for damage or moisture.

Test back-up battery by pulling the fuse service system, light will come on (if applicable).

Test engine shutdown (if applicable).

Install new safety seals, stickers, and complete all associated paper work accordingly.

Bottle dates shall be 6 years for a Teardown and 12 years for Hydro-test.

Squib dates shall be 3 years field life and 5 years shelf life for Amerex.

Linear actuator dates shall be 6 years field life and 12 years shelf life for Amerex.