| COUNTY OF FRESNO |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ADDENDUM NUMBER: TWO |  |  |  |  |  |  |  |  |  |
|  |  |  | RFQ NUMBER: |  |  |  |  |  |  |
| January 16, 2007 |  |  |  |  |  |  |  |  |  |
|  |  |  |  | PURCHASING USE |  |  |  |  |  |
|  |  | ORG/Requisition: 9020/ 9027000001 |  |  | CJN | /tmp/in/input.doc |  |  |  |
|  | IMPORTANT: SUBMIT QUOTATION IN SEALED PACKAGE WITH QUOTATION NUMBER, CLOSING DATE AND BUYER’S NAME MARKED CLEARLY ON THE OUTSIDE TO: |  |  |  |  |  |  |  |  |
|  | COUNTY OF FRESNO, Purchasing 4525 EAST HAMILTON AVENUE FRESNO, CA 93702-4599 |  |  |  |  |  |  |  |  |
|  | Closing date of bid will be at 2:00 p.m., on January 23, 2007. QUOTES WILL BE CONSIDERED LATE WHEN THE OFFICIAL PURCHASING TIME CLOCK READS 2:00 P.M. |  |  |  |  |  |  |  |  |
|  | Quotes will be opened and publicly read at that time. All quotation information will be available for review after contract award. |  |  |  |  |  |  |  |  |
|  | Clarification of specifications are to be directed to: Craig Nickel, phone (559) 456-7110, FAX (559) 456-7831. |  |  |  |  |  |  |  |  |
|  | NOTE THE following and attached ADDITIONS, DELETIONS AND/or CHANGES TO THE REQUIREMENTS OF REQUEST FOR QUOTATION NUMBER: AND INCLUDE THEM IN YOUR RESPONSE. PLEASE SIGN AND RETURN THIS ADDENDUM WITH YOUR QUOTATION. - THE CLOSE DATE HAS BEEN CHANGED TO JANUARY 23, 2007 AT 2:00 P.M. - INCLUDED IN THIS ADDENDUM: - ANSWERS TO QUESTIONS ASKED BY BIDDERS. - SJVAPDCD PERMIT TO OPERATE - DOCUMENTS PERTAINING TO WASTE DISCHARGE REQUIREMENTS (3 PAGES). |  |  |  |  |  |  |  |  |

| ACKNOWLEDGMENT OF ADDENDUM NUMBER TWO TO RFQ |  |  |
| --- | --- | --- |
| COMPANY NAME: |  |  |
| (PRINT) |  |  |
| SIGNATURE: |  |  |
| NAME & TITLE: |  |  |
| (PRINT) |  |  |

Request for Quotation

Number 928-4351

Landfill Gas Collection System Maintenance and Operation

Southeast Regional Disposal Site

Brady Environmental Inc. December 22, 2006

Additional Contractor Questions

- First Bullet –

  - Various questions are asked regarding perimeter probe monitoring.

Response – The perimeter probe monitoring is performed and reported to regulatory agencies by County personnel.  Therefore, it is not included in the scope of work for this RFQ.

- Second Bullet –

  - Can we obtain a copy of the APCD approved surface emission testing protocol, as required by Rule 4642 section 6.1.1?

Response – No APCD approved surface emission testing protocol exists for the site.  The scope of Task 2 of this RFQ is worded the same as the previous agreement for this work.

  - Has the site failed a surface emission test in the past two years?

Response – No.  In addition, in accordance with Rule 4642, since the site has not failed a surface emission test within the last two semi-annual tests, surface emission testing at the site is currently performed annually.  Therefore, under Task 2 (page 11 of the RFQ) the frequency of both Testing and Reporting is amended to annually.  Additionally, in the quotation schedule on page 15, Task 2 Testing and Reporting are amended to be bid at a single annual rate.

  - What is the approved wind measurement method and location of anemometer?

Response – Please see response to question 2.a. above.

  - Can the rain station at the near-by Selma Airport be used to confirm compliance with the “no rain 72 hours prior to the test” requirement?

Response – Yes.

- Third Bullet –

  - Would it be possible to obtain a copy of the landfill’s existing operating permit issued by the San Joaquin Valley Air Pollution Control District (APCD) and the Waste Discharge Requirements (WDRs) issued by the Regional Water Quality Control Board?

Response – A copy of the two-page APCD Permit to Operate accompanies this response as Attachment A.  Please keep in mind that relative to some requirements of APCD Rule 4642, the landfill gas (LFG) flare is an open flare and was grandfathered under some regulations as it was installed and permitted prior to July 20, 1995.

A review of the WDRs Order No. 99-124 for the site revealed only four references to LFG or gas condensate: two in the WDRs (Discharge Specifications B.3. & B.4.) and two within the Standard Provisions and Reporting Requirements dated August 1997 (STANDARD CONDITIONS, Operations Item No. 6 and Post-Closure Item No. 2) The applicable pages from these documents accompany this response as Attachment B, Pages B-1 through B-3.

For additional clarification, the three references on page 10 of the RFQ of “where applicable” are deleted.  The use of this term was not intended to qualify any monitoring or testing relative to any regulatory requirements.  The original intent of the phrase “where applicable” was so that only specific wells or headers ports need be monitored “where applicable” during a re-inspection.

- Fourth Bullet –

  - In the monthly maintenance task, you indicate that the condensate traps should be drained.

Response – There are no water or condensate traps in the LFG System.  The first bullet under the Maintenance - Monthly section on page 11 of the RFQ (Drain/purge water/condensate traps) will be deleted and replaced with the following:  Inspect header piping and laterals audibly and through pressure measurements to ensure proper LFG flow and condensate drainage back into the active gas extraction wells.

  - From observations of the site on December 20, 2006, condensate is drained back into the active extraction well or wells specifically designed to allow condensate to drain back into the waste column.  Do these wells require periodic pumping to remove excess condensate?

Response – No. If it should become necessary, such work would be covered under Extra Services portion of the Agreement.

  - Shall these condensate wells be sounded on a periodic basis?

Response – No.  If it should become necessary, such work would be covered under Extra Services portion of the Agreement.

  - Can these condensate wells be used to dispose of condensate accumulation at the blower and flare station?

Response – No, however, to our knowledge there is no condensate accumulation at the blower and flare station.

- Fifth Bullet –

  - Flow rate measurements at each well head: during the site walk on December 20, 2006, no flow meters (orifice plate, pitot tubes or access ports for portable flow meters) were observed at the well heads, only pressure tabs.  Will the contractor be required to measure flow rates at each wellhead?

Response – No.  Accordingly, the Task 1, Monitoring Monthly bullet list will be modified as follows:  Wellhead pressure vacuum and flow (where applicable).  In addition, for consistency the next following bullet will be modified as follows:  Header pressure vacuum (where applicable).

- Sixth Bullet

  - Quarterly structure monitoring:  Can you confirm that structure monitoring is only for the old scale house and the bathroom building?  If not, what other buildings require monitoring?

Response – The only two structures to be monitored quarterly are the old scale house and the bathroom.

- Seventh Bullet –

  - Telemetry: during the site walk, it was indicated that no site telemetry exists.  Can we obtain information on what telemetry exists, if present, for the system operation?

Response – There is currently no operational telemetry for the LFG System operation at the site.  The second bullet under the Maintenance - Monthly section on page 11 of the RFQ (Test alarm signals (telemetry system)) will be deleted.

- Eighth Bullet –

  - Can you define emergency?

Response – In the RFQ on page 12, Task 4 - Emergency Maintenance defines the circumstances or events under which an Emergency Maintenance response by the contractor is to take place.  However, as discussed in question 7a above, on page 12 of the RFQ, under Task 4 – Emergency Maintenance, the first bullet is revised as follows, “Emergency response requests due to site telemetry alarms or at request of County staff”.