## Sheet1
DATE | LOCATION | PROBLEM | SOLUTION
2009-01-01 | MJ-3A | REPORT CLAIMS WHEN DOOR FOR 3A-12 IS SHAKEN 3A-14 UNLOCKS. | REPLACED DOOR CARD FOR 3A-12 AND LOCKSMITH PERFORMED OTHER POSSIBLE PROBLEMS. C/O
2009-01-02 | MJ-4C | DOORS 4C10 THROUGH 4C16 ALL WERE FLASHING RED EVEN WHEN DOORS WERE SECURE. | REPLACED DOOR CARDS FOR A COUPLE OF DOORS, PROBLEM IS FIXED. C/O
2009-01-02 | MJ-4 | DOOR 4084E GOES FROM GREEN TO RED ON CONTROL SWITCH. | LOCKSMITH CORRECTED PROBLEM. C/O
2009-01-02 | MJ-4 | 4A-14 INTERCOM WON’T CALL INTO SECURITY. | REPLACED INTERCOM SWITCH. C/O
2009-01-04 | SAJ-1 | 1ST FLOOR SECURITY DOOR LOCK WAS SMOKING. | REPLACED SOLID STATE RELAY AND HAD LOCKSMITH REPLACE LOCK. C/O
2009-01-04 | MJ-5 | ELEVATOR #1 DOOR SWITCH IS BROKEN IN SECURITY STATION. | REPLACED BROKEN PADDLE.C/O
2009-01-04 | NAJ-1 | CENTRAL CONTROL REAR HALL DOOR DOES NOT UNLOCK. | PANEL FUNCTIONS ALL CHECK GOOD, LOCK ADJUSTMENT PROBLEM. C/O
2009-01-05 | MJ-2 | ZONE #1 ALARM DIVERTOR #14 HAS A STUCK TUBE. | REMOVED STUCK TUBE RESET SYSTEM.
2009-01-05 | MJ-2 | CENTRAL CONTROL BROKEN INTERCOM SWITCH. | REPLACED BROKEN SWITCH PADDLE.
2009-01-05 | MJ-4 | BROKEN TOGGLE SWITCH FOR VISITING DOOR. | REPLACED SWITCH TOGGLE.C/O
2009-01-05 | MJ-1 | LOBBY OUTER RELEASE DOOR HAS SHORTED SWITCH. | REPLACE DOOR CONTROL SWITCH. C/O
2009-01-06 | MJ-5 | CELL 5B-8 WON’T CALL INTO SECURITY. | REPLACED INTERCOM SWITCH.
2009-01-06 | NAJ-4 | POD-C HEAT DETECTOR RESTROOM COMING IN NO ANSWER. | REPLACED HEAT DETECTOR BASE.
2009-01-07 | MJ-1 | SMOKE DETECTOR IN ELEVATOR #4 VESTIBULE APPEARS LOOSE. | REPLACED SMOKE DETECTOR.
2009-01-07 | NAJ-4 | TUBE STUCK IN STATION #42. | REMOVED STUCK TUBE DUE TO HEAVY MAIL.
2009-01-07 | MJ-CC | 4TH FF HALLWAY CAMERA LOOKING NORTH HAS BAD VIDEO. | REPLACED CABLE FITTINGS ON CAMERA , DIST AMP, CENTRAL CONTROL.
2009-01-07 | MJ-5 | UPPER FIRE DOOR SHOWS RED WHEN SECURE. | LOCK NEEDED TO BE LUBRICATED. SHOWS SECURE.
2009-01-07 | MJ-5 | UPPER FIRE DOOR BETWEEN PODSB AND C SHOW RED. | LOCK WAS VERY DRY AND REQUIRED WD-40.
2009-01-08 | NAJ-4 | TUBE STATION #42 IS VERY WEAK. | REMOVED MAIL FROM TRAP ABOVE COURT HOLDING.
2009-01-09 | NAJ-1-CC | ELEVATOR #2 INTERCOM SWITCH IS BROKEN. | REPLACED SWITCH PADDLE. C/0
2009-01-09 | MJ-5 | INTERCOM SWITCH 5A-6 HAS A BROKEN PADDLE. | REPLACED SWITCH PADDLE.
2009-01-09 | NAJ-2 | TUBE STATION IN 2ND FLOOR SECURITY IS DOWN. | RESET SYSTEM.
2009-01-10 | SAJ-1 | SECURITY CAMERA FOR DORM C IS OUT. | REPROGRAMMED CALL-UP SWITCHER. C/O
2009-01-10 | MJ-5 | BROKEN TOGGLE SWITCH FOR INMATE VISITING DOOR. | REPLACED SWITCH PADDLE. C/O
2009-01-12 | MJ-5 | CELL 5E4 INTERCOM SWITCH BROKEN. | REPLACED INTERCOM SWITCH PADDLE.
2009-01-13 | SAJ-2 | INTERCOM DOES NOT WORK TO F& G AREA. | REPLACED MICROPHONE AND RESET ALL CALL. C/O
2009-01-13 | SAJ-1 | DORM-B CAMERA IN SECURITY HAS NO PICTURE. | REPLACED CCTV FITTING AT M-STREET SWITCHER. C/O
2009-01-14 | SAJ-2 | INTERCOM RESET BUTTON AND MASTER UNLOCK. | REPLACED INTERCOM RESET BUTTON AND MASTER UNLOCK.
2009-01-14 | SAJ-3 | INTERCOM RESET BUTTON AND MASTER UNLOCK. | REPLACED INTERCOM RESET BUTTON AND MASTER UNLOCK.
2009-01-14 | NAJ-2 | ELEVATOR #2 INTERCOM ALWAYS STAYS ON. | REPLACED SWITCH.
2009-01-14 | MJ-5 | CELL DOOR 5B10 WON’T UNLOCK FROM SWITCH. | REFERRED PROBLEM TO LOCKSMITH.
2009-01-14 | MJ-5 | INTERCOM SWITCHES 5B14 AND 5E HAVE BROKEN SWITCHES. | REPLACED BROKEN SWITCH PADDLES.
2009-01-14 | SAJ-1 | DOOR CONTROL SWITCH FOR DORM VESTIBULE DOOR IS BROKEN. | REPLACED BROKEN SWITCH PADDLE. C/O
2009-01-15 | SAJ-3 | INTERCOM SYSTEM SECURITY CAN’T HEAR INMATES. | REPAIRED MICROPHONE CABLE.
2009-01-16 | MJ-2 | TUBE SYSTEM DIVERTOR #21 IN NAJ-CC LEAKING AIR. | RE-POSITIONED AIR CYLINDER ON DIVERTER AND RESTARTED COMPRESSOR.
2009-01-19 | MJ-5 | CELL 5B-13 CAN’T CALL IN TO SECURITY STATION. | REPAIRED CALL-IN BUTTON IN CELL.
2009-01-19 | MJ-1 | BBLEM FOUND.OOKING CAMERA THAT LOOKS AT THE PAT DOWN AREA IS OUT. | REPLACED CAMERA, POWER SUPPLY ON CAMERA BAD C/O
2009-01-20 | SAJ-3 | CHECK INTERCOM SYSTEM NOT WORKING PROPERLY. | CHECKED SYSTEM WORKING PROPERLY.
2009-01-20 | SAJ-3 | POD-C DORM SPEAKER SOUNDS DISTORTED. | CHECK AND NO PROBLEM FOUND.
2009-01-21 | MJ-5 | INTERCOMS A5,A9,B3,F6,AND F9 DON’T CALL-IN. | REPLACED SITCH FOR A5 AND REPLACED LED’S FOR ALL OTHERS.
2009-01-21 | MJ-4 | GYM DOOR CONTROL SWITCH IS BROKEN. | REPLACED DOOR CONTROL SWITCH.
2009-01-21 | NAJ-4 | MASTER UNLOCK BUTTONE ON A AND B CONSLOLE ARE HRAD TO OPERATE. | REPLACED MASTER UNLOCK ON BOTH A AND B PANELS.
2009-01-21 | NAJ-4 | INTERCOM REST BUTTON ON A PANEL HARD TO OPERATE. | REPLACED SWITCH.
2009-01-22 | MJ-4 | INTERCOM ON ABC SIDE IS INTERMITTEN. | REPLACED MICROPHONE.
2009-01-22 | MJ-6 | INTERCOM FOR CELL 6A-8 NOT WORKING. | CHECK AND FOUND NOTHING WRONG.
2009-01-22 | NAJ-4 | NODE 2 FIRE ALARM PANEL HAS A GROUND FAULT. | REPLACED POWER SUPPLY.
2009-01-24 | SAJ-2 | FIRE ALARM SYSTEM HAS A FLOATING EARTH GROUND. | INSTALLED RESISTOR ON NEGATIVE SIDE OF POWER SUPPLY. C/O
2009-01-24 | NAJ-1 | CENTRAL CONTROL OUTER WEST HALL DOOR WON’T OPEN. | INTERLOCK WAS TURNED ON. C/O
2009-01-25 | NAJ-BSMT | ALL DOOR LOCKS LOST POWER. | POWER SUPPLY DIED. REPLACED POWER SUPPLY. C/O
2009-01-26 | MJ-1 | LOBBY REAR RELEASE DOOR CAUSINGINTERLOCK PROBLEMS. | REPLACED DOOR CONTROL CARD.
2009-01-26 | NAJ-2 | MICROPHONE FOR DEF SIDE IS INTERMITTEN. | AUDIO LEVEL TOO HIGH AND ADJUSTED REED SWITCH.
2009-01-26 | NAJ-2 | MASTER UNLOCK BUTTONS HARD TO OPERATE. | REPLACED MASTER UNLOCKS BOTH CONSOLES AND INTERCOM RESET ON B CONSOLE.
2009-01-26 | MJ-1 | LOBBY RELEASE DOORS ARE INTERLOCKING RANDOMLY. | REPLACED DOOR CARD FOR DOOR 1033B.
2009-01-27 | MJ-1 | LOBBY DOORS STILL INTERLOCKING. | REPLACED DOOR CONTROL SWITCH FOR 1033B CLOSEST TO WINDOW.
2009-01-28 | MJ-1 | LOBBY SECURITY CENTER MONITOR THAT LOOKS AT BONDROOM IS OUT. | REPLACED MONITOR.
2009-01-28 | SAJ-2 | INTERCOM CALL IN FOR 2D SHOWER CALLS IN INTERMITTEN. | ADJUSTED INTERCOM SWITCH.
2009-01-29 | NAJ-3 | GYM SPEAKER NOT WORKING. | INSTALLED GUARD AROUND HORN AND REPAIRED SMASHED WIRE IN INTERCOM LOCATED IN COLUMN.
2009-01-29 | MJ-1 | MAIN JAIL LOBBY TUBE STATION NOT WORKING. | RESET TUBE SYSTEM.
2009-01-30 | MJ-5 | SECURITY STATION DOOR DOESN’T SHOW SECURE. | FOUND NOTHING WRONG.
2009-02-02 | MJ-1 | SERVER ROOM #1025 HAS TROUBLE ON FM200 PANEL. | AUX POWER SUPPLY BATTERIES REPLACED.
2009-02-02 | SAJ-2 | FIRE ALARM SYSTEM HAS A TROUBLE, DIRTY DETECTOR FOR 2D12. | REPLACED SMOKE DETECTOR.
2009-02-02 | MJ-2 | TUBE SYSTEM IS IN ALARM. | RESET GONE MESSAGE ON TUBE SYSTEM.
2009-02-02 | MJ-5 | 5E POD GROUP UNLOCK HAS BROKEN PADDLE. | REPLACED PADDLE.
2009-02-03 | MJ-6 | 6E-9 CELL DOOR CAN’T UNLOCK WITH KEY. | REFERRED PROBLEM TO LOCKSMITH.
2009-02-03 | MJ-2 | V2 SALLYPORT EXIT GATE FLASHES RED INTERMITTENLY. | REPLACED CONTROL CARD.
2009-02-05 | MJ-1 | LOBBY TUBE STATION INALARM. | REPLACED FUSE AND RESET SYSTEM.
2009-02-06 | SAJ-BSMT | COURT HOLDING QUAD MONITOR NEEDS EXTENSION ON CABLE TO MOVE. | INSTALLED EXTENSION POWER SURGES.CABLE ONVIDEO FEED.
2009-02-08 | MJ-5 | FIRE ALARM WON’T RESET. | BYPASSED ZONE DUE TO WATER LEAK FROM 6D. C/O
2009-02-09 | MJ-2 | CENTRAL CONTROL HAS BROKEN TOGGLE SWITCH FOR CENTRAL CONTROL ENTRY DOOR. | REPLACED BROKEN PADDLE. C/O
2009-02-10 | SAJ-4 | 4-POSITION SWITCHER NOT WORKING FOR YARD CAMERAS. | REPLACED SWITCHER DUE TO .POWER SURGES.
2009-02-10 | MJ-2 | TUBE SYSTEM HAS INTER ZONE STALL. | RESET SYSTEM.
2009-02-11 | NAJ-4 | TUBE STATION IN SECURITY UNABLE TO SEND TUBES. | ADJUSTED MAGNETIC SWITCH THAT WAS OUT OF ADJUSTMENT.
2009-02-11 | NAJ-4 | POD-D DOOR LOCK SWITCH VERY HARD TO OPERATE. | REPLACED 3-POSITION SWITCH
2009-02-11 | SAJ-2 | SECURITY STATION HAS NO RADIO. | REPLACED 125WATT AMPLIFIER IN SECURITY STATION.
2009-02-11 | MJ-2 | TUBE SYSTEM HAS NUMEROUS ZONE STALLS. | DIVERTOR #24 IN MAIL ROOM AIR CYLINDER HOSES RE ROUTED.
2009-02-12 | MJ-3 | 3C-14 INTERCOM SWITCH HAS BROKEN PADDLE. | REPLACED SWITCH PADDLE.
2009-02-12 | SAJ-1 | METAL DETECTOR ON 1ST FLOOR IS UNPLUGGED. | CLEANED METAL DETECTOR AND POWERED UP UNIT.
2009-02-12 | MJ-2 | INFIRMARY SIDE BRIEFING DOOR INTERCOM DOESN’T ALWAYS LIGHT UP. | REPLACED CALL IN SWITCH IN THE FIELD.
2009-02-12 | MJ-5 | POD-A DOOR WON’T UNLOCK FORM SECURITY OR WITH KEY. | REFERRED PROBLEM TO LOCKSMITH.
2009-02-13 | MJ-1 | BOOKING MALE INTAKE SWITCH FOR DOOR NOT OPERATING PROPERLY. | REPLACED DOOR CONTROL SWITCH.
2009-02-13 | SAJ-4 | E-VESTIBULE CAMERA HAS A POOR PICTURE. | REPLACED CAMERA.
2009-02-13 | SAJ-4 | E-POD SLIDER DOOR NOT WORKING. | FOUND NOTHING WRONG, DOOR OPERATING.
2009-02-13 | MJ-5 | 5B-4 INTERCOM SWITCH PADDLE BROKEN. | REPLACED SWITCH PADDLE.
2009-02-13 | MJ-3 | VISITING INTERCOM SWITCH IS BROKEN. | REPLACED SWITCH PADDLE.
2009-02-13 | MJ-2 | INFIRMARY LIGHT SWITCH ON SECURITY PANEL NOT WORKING. | REPLACED SWITCH AND STILL A PROBLEM REFERRED TO LOCKSMITH.
2009-02-15 | MJ-5 | FIRE ALARM WON’T REST, WATER LEAK BETWEEN 5A7 & 5A8. | REPLACED SMOKE DETECTOR IN CHASE. C/O
2009-02-16 | MJ-4 | SECURITY S/W SALLYPORT DOOR BROKEN SWITCH. | REPLACED DOOR CONTROL SWITCH.
2009-02-16 | SAJ-1 | DORM C CABLE TV FITTING IS LOOSE. | REPLACED WALL FITTING AND CABLE.
2009-02-17 | MJ-5 | GYM REAR ENTRY DOOR SHOWS RED WHEN SECURE. | CHECKED DOOR AND NO PROBLEM FOUND.
2009-02-18 | MJ-6 | INTERCOM SWITCH FOR 6A8 NOT WORKING. | REPLACED INTERCOM SWITCH.
2009-02-19 | MJ-6 | TUBE STATION #1 LOADER NOT WORKING | REPLACED FUSE RESET STATION.
2009-02-22 | NAJ-CC | CENTRAL CONTROL MONITOR FOR TUNNEL IS OUT. | VIDEO MOTION DETECTOR WAS TURNED OFF. TURNED ON TO RESTORE VIDEO. C/O
2009-02-23 | MJ-2 | TUBE STATION #11 NOT WORKING. | LOADER ARM LOOSE, REFASTEDED LOADER ARM STATION OPERATING.
2009-02-23 | MJ-2 | 1ST FLOOR SECURITY CAMERA VIDEO IS BAD. | REPLACED CABLE FITTING AT DISTRIBUTION AMPLIFIER END. GOOD SIGNAL.
2009-02-23 | NAJ-2 | 2ND FLOOR METAL DETECTOR MALFUNCTIONING. | RE SEATED CABLES ON UNIT AND RESET.
2009-02-23 | MJ-2 | SALLYPORT EXIT GATE HAS BROKEN TOGGLE SWITCH. | REPLACED BROKEN TOGGLE.
2009-02-25 | NAJ-1 | 9-INCH LOBBY MONITOR IS OUT. | REPLACED MONITOR.
2009-02-25 | SAJ-3 | SECURITY STATION DOOR WHEN LOCKED STAYS UNLOCKED. | REFERRED PROBLEM TO LOCKSMITH.
2009-02-25 | NAJ-5 | SECURITY STATION MINICOM BOX #21 IS NOT WORKING. | RESET SYSTEM.
2009-02-26 | SAJ-2 | CENTRAL TUNNEL DOOR INTERCOM SWITCH CAUSING CAMERA TO LOCK IN ALARM. | REPLACED INTERCOM SWITCH.
2009-02-26 | NAJ-1 | CENTRAL CONTROL FIRE ALARM HAS TROUBLE. NODE #2 MISSING | REPLACED CPU BOARD AND RE-LOADED PROGRAM.
2009-02-27 | MJ-2 | CENTRAL CONTROL OUTER ENROUTER DOOR CONTROL SWITCH NOT WORKING. | REPLACED DOOR CONTROL SWITCH.
2009-03-02 | SAJ-3 | POD-A INTERCOM CUTS IN AND OUT. | FOUND NOTHING WRONG
2009-03-04 | NAJ-1 | CENTRAL CONTROL DOOR CONTROL COMPUTER SHUT DOWN. | RESET COMPUTER. C/O B.
2009-03-04 | MJ-2 | CENTRAL CONTROL SWITCH 1051A BAD. | REPLACED DOOR CONTROL SWITCH.
2009-03-04 | MJ-2 | CENTRAL CONTROL SWITCH 1052A IS BAD. | REOLACED DOOR CONTROL SWITCH.
2009-03-04 | MJ-5E | POD-E INTERCOM SPEAKER HANGING FROM CABLE. | REPLACED VANDALIZED SPEAKER BRACKET.
2009-03-04 | SAJ-BSMT | PROGRAM ROOM HAS A BAD CAMERA. | REPLACED CAMERA.
2009-03-04 | NAJ-2 | CENTRAL CONTROL COMPUTER MAINTENANCE. | SHUT DOWN COMPUTER FOR MAINTENANCE.
2009-03-05 | SAJ-1 | M-STREET SECURITY INMATE VISITING VESTIBULE DOOR WON’T SECURE. | REPLACED RELAY AND SWITCH. C/OB.
2009-03-06 | MJ-2 | CELL 2B4 INTERCOM DOES NOT LIGHT UP WHEN PRESSED. | CHECKED INTERCOM WITH OFFICER AND FOUND NOTHING WRONG.
2009-03-06 | MJ-2 | INTERCOM 2ND FLOOR BY ISO CELL WON’T LIGHT UP IN CENTRAL. | REPLACED SWITCH IN CENTRAL CONTROL.
2009-03-06 | MJ-6 | TUBE SYSTEM DOWN NORTH JAIL FACILITY. | REPLACED COMPRESSOR PUMP IN NORTH JAIL.
2009-03-07 | NAJ-1 | CENTRAL CONTROL DOOR CONTROL COMPUTER SHUT DOWN. | RE BOOTED SYSTEM AND LOGGED ON. C/O B
2009-03-08 | NAJ-1 | CENTRAL CONTROL FIRE ALARM TROUBLE ON NODE 2 GROUND FAULT. | COLD START NODE 2 C/OB.
2009-03-09 | NAJ-1 | LOBBY TUBE STATION IS DOWN. | SYSTEM COMPRESSOR BAD. REPLALCED COMPRESSOR.
2009-03-09 | MJ-4 | SPEAKER IN POD C INMATES CAN’T HEAR. | CHANGED MICROPHONE SETTINGS, CHECKED OK.
2009-03-10 | MJ-5 | POD-D SMOKE DETECTOR NEXT TO SHOWER IN ALARM. | REPLACED DETECTOR DUE TO WATER LEAK FROM 6TH FLOOR POD LEAK.
2009-03-10 | NAJ-2 | INTERCOM ON A PANEL SYAYS LITE, WON’T RESET. | CHECKED AND REPLACED INTERCOM RESET BUTTON ON A PANEL.
2009-03-10 | NAJ | RESET TIME ON ALL LEVELS OF FACILITY. | RESET TIME.
2009-03-10 | NAJ | CHECK ALL SECURITY PANELS. | REPLACED SEVERAL CONTROL BUTTONS ON PANEL.
2009-03-11 | MJ-BKG | DVR IN SGT.’S OFFICE NEEDS TIME CHANGED. | CHANGED TIME.
2009-03-13 | MJ-2 | CENTRAL CONTROL DOOR INDICATION FOR 6FF8 SHOWS UNSECURE. | FOUND NOTHING WRONG.
2009-03-13 | MJ-2 | CENTRAL CONTROL DOOR INDICATION FOR ELEV. 3 DOOR SHOWS UNSECURE. | FOUNFD NOTHING WRONG.
2009-03-17 | SAJ-VISIT | CHECK FEMALE PHONE WIRES PULLED AWAY. | CHECKED ALL PHONES AND REPLACED (2) REPAIRED (1).
2009-03-17 | MJ-6 | SECURITY STATION ALL DOORS ON A,B,C, SIDE SHOW DOUBLE LIGHT INDICATION. | VISITING PHONE #2 VISITORS SIDE CAUSING MAJOR POWER SUPPLY SHORT.
2009-03-17 | MJ-6 | VISITING PHONES NEED TO BE CHECKED. | CHECKED ALL VISITING PHONES AND REPLACED (2).
2009-03-18 | NAJ-4 | VISITING PHONES NEED TO BE CHECKED. DOOR. | CHECKED ALL PHONES AND REPLACED (2).
2009-03-18 | MJ-2 | BOOKING CAMERA FOR PAT DOWN AREA HAS NO VIDEO. | REPLACED FITTING CAMERA INPUT AT DISTRIBUTION AMP.
2009-03-18 | SAJ-1 | M-STREET FEMALE VISITING SLIDER DOOR SHOWS UNSECURE. | LOCKSMITH ADJUSTED SWITCH AT TOP OF THE DOOR.
2009-03-19 | SAJ-1 | ATTORNEY LOBBY INTERVIEW AREA HAS PLUMBING LEAK IN CUBICAL CAUSING FIRE ALARM. | REMOVED SMOKE DETECTOR AND BYPASSED DETECTOR UNTIL LEAK IS FIXED.
2009-03-23 | MJ-6 | MICROPHONE ON D,E,F SIDE NOT WORKING. | REPLACED MICROPHONE.
2009-03-23 | MJ-6 | CELL DOORS C2,C3,F2,F3,F9,F1,CHECKED GOOD OPERATION FROM KEY AND CONSOLE. | CECKED ALL DOORS LISTED.
2009-03-23 | MJ-6 | 6E-13 LOCK IS VERY HOT. | REFERRED TO COUNT LOCKSMITH.
2009-03-23 | SAJ-3 | CELL 3G3 INTERCOM STICKS ON. | CHECKED AND FOUND NOTHING WRONG.
2009-03-23 | MJ-4 | CELL DOOR 4F16 SHOWS RED WHEN SECURE. | REPLACED DOOR CONTROL SWITCH.
2009-03-23 | MJ-BSMT | DOOR B5 TUNNEL DOOR DOESN’T SHOW A RED INDICATION. | REPLACED DOOR INTERFACE CARD.
2009-03-24 | MJ-2 | CENTRAL CONTROL DOOR 1054B OUTER STAFF ENTRY DOOR UNLOCKS BY ITSELF. | REPLACED DOOR CONTROL SWITCH.
2009-03-24 | MJ-4 | POD-C FIRE ALARM WON’T RESET. | REPLACED SMOKE DETECTOR BETWEEN C7 AND C8.
2009-03-24 | MJ-6 | STATION #1 LOADER NOT WORKING PROPERLY. | REPLACED CAM ARM CHECKED OK.
2009-03-26 | NAJ-4 | FIRE ALARM TROUBLE POD-C PLUMBING CHASE. | REPLACED DETECTOR.
2009-03-26 | MJ-6 | S/W SALLYPORT DOOR SHOWS RED WHEN SECURE. | REFERRED PROBLEM TO LOCKSMITH.
2009-03-26 | MJ-2 | POD-D INTERCOM SPEAKER VANDALIZED BY INMATE. | REPAIRED SPEAKER GRILL.
2009-03-26 | MJ-2 | POD-D UPPER LEVEL MISSING COVER PLATE. | REPLACED COVER PLATE.
2009-03-26 | NAJ-1 | CENTRAL CONTROL S/W STAIRWELL DOOR SHOWS FLASHING RED WHEN SECURE. | FOUND NOTHING WRONG IN CENTRAL CONTROL.
2009-03-26 | MJ-1 | LOBBY REAR RELEASE DOOR ON THORN PANEL CAUSING INTERLOCK PROBLEMS. | REPLACED REAR RELEASE DOOR SWITCH.
2009-03-30 | SAJ-2 | CELL 2D-16 FLASHES RED WHEN SECURE. | REFERRED PROBLEM TO THE LOCKSMITH.
2009-03-30 | MJ-5 | INTERCOM SYSTEM NOT WORKING PROPERLY. | CHECKED MICROPHONES ON BOTH SIDES OF SECURITY, FOUND NOTHING WRONG.
2009-03-31 | NAJ-1 | VACUM FOR TUBE SYSTEM IN NORTH ANNEX JAIL IS WEAK. | REMOVED LOOSE MAIL IN TRAP AT DIVERTOER #20.
2009-04-02 | MJ-2 | INTERCOM NOT WORKING FOR DOOR BY INFIRMARY. | CHECKED OPERATION FOUND NOTHING WRING.
2009-04-03 | MJ-2 | CENTRAL CONTROL TIME OFF ON MONITORS. | RESET TIME ON PELCO SYSTEM.
2009-04-06 | MJ-6 | CELL F16 CONTROL PANEL LIGHTS ARE OUT. | CHECKED INTERCOM AND DOOR LIGHTS ALL CHECKED OK.
2009-04-06 | MJ-2 | CENTRAL CONTROL 2ND FLR SECURITY CAMERA NOT WORKING. | RE-TERMINATED FITTING CAMERA SIGNAL CHEKS GOOD.
2009-04-07 | MJ-4 | POD E DOOR SWITCH BROKEN. | RELOACED SWITCH PADDLE.
2009-04-07 | SAJ-2 | 2D SHOWER INTERCOM ALWAYS STAYS ON. | REPLACED INTERCOM SWITCH DUE TO CORROSION.
2009-04-07 | NAJ-2 | SECURITY TUBE STATION NOT WORKING. | RESET ZONE, SYSTEM NORMAL.
2009-04-07 | SAJ-1 | ATTORNEY LOBBY SMOKE DETECTOR KEEPS GOING IN ALARM. | REPLACED CORRODED SMOKE DETECTOR BASE. SYSTEM NORMAL.
2009-04-08 | MJ-2 | INFIRMARY DOOR TO STAFF SIDE INTERCOM DOESN’T ALWAYS LIGHT IN CENTRAL CONTROL. | REPLACED INTERCOM STATION.
2009-04-08 | SAJ-2 | FIRE ALARM IN LAUNDRY AREA STAYING IN ALARM. | REPLACED DIRTY SMOKE DETECTOR IN DRYER AREA.
2009-04-09 | MJ-1 | LOBBY TUBE STATION NOT WORKING. | REPLACED LOADER MOTOR STATION MORMAL.
2009-04-09 | MJ-4 | 4F-2 INTERCOM DOESN’T ACTIVATE IN SECURITY STATION. | REPLACED INTERCOM SWITCH.
2009-04-09 | MJ-2 | CENTRAL CONTROL OUTER STAFF ENTRY DOOR HAS BROKEN TOGGLE. | REPLACED BROKEN TOGGLE.
2009-04-09 | NAJ-3 | POD-BINTERCOM INMATES CAN’T HEAR AUDIO FROM SECURITY. | FOUND NOTHING WRONG.
2009-04-10 | SAJ-1 | HALL DOOR IN F HALLWAY SHOWS RED WHEN SECURE. | REFERRED PROBLEM TO LOCKSMITH.
2009-04-11 | NAJ-3 | ABC MICROPHONE NOT WORKING. | REPLACED MICROPHONE. C/O
2009-04-13 | MJ-2 | TUBE STATION #11 LOADER ARM IS LOOSE. | REPLACED LOADER ARM. STATION NORMAL.
2009-04-13 | MJ-2 | VACUM IS VERY WEAK ON TUBE SYSTEM IN MAIN JAIL. | REPLACED 1-VACUM MOTOR.
2009-04-14 | MJ-3 | INTERCOM ON ABC SIDE HAS CROSS TALK WITH OTHER CELLS. | ADDED ISOLATION TRANSFORMERS ON AUDIO SIDE ALONG WITH RESISTORS.
2009-04-15 | SAJ-BSMT | LAUNDRY AREA HAS NO RADIO PLAYING. | REPLACED VOLUME CONTROL IN LAUNDRY OFFICE.
2009-04-15 | MJ-3 | BROKEN TOGGLE SWITCH FOR 3A3. | REPLACED BROKEN TOGGLE FOR 3A3.
2009-04-16 | NAJ-4 | POD-F DOOR SHOWS RED WHEN DOOR IS SECURE. | CHECKED AND FOUND DOOR IS SAGGING REFERRED TO MAINTENANCE.
2009-04-16 | NAJ | CHECKED ALL HOUSING FLOORS FOR WORN BUTTONS ON CONTROL PANELS. | REPLACED SEVERAL DOOR CONTROL BUTTONS.
2009-04-16 | MJ-1 | BOND ROOM #3 HAS A BROKEN PHONE. | REPLACED PHONE.
2009-04-16 | SAJ-2 | CENTRAL CONTROL ELEVATOR #1 MONITOR WENT OUT. | REPLACED MONITOR.
2009-04-17 | SAJ-1 | ATTORNEY LOBBY INTERCOM CAN’T HEAR IN THE INTERVIEW AREA. | RESET SYSTEM AND TESTED.
2009-04-19 | MJ-4 | CELL CHASE BETWEEN C15 &C16 HAS A WATER LEAK CAUSINF FIRE ALARM. | REMOVE SMOKE DETECTOR UNTIL LEAK IS REPAIRED. C/O
2009-04-20 | MJ-6 | 6D-1 INTYERCOM DOESN’T CALL INTO SECURITY STATION. | INTERCOM WAS ACTIVATED AND FOUND NOTHING WRONG.
2009-04-21 | MJ-2 | CENTRAL CONTROL ELEVATOR #3 MONITOR GOES GREEN AND FLICKERS. | REPLACED MONITOR.
2009-04-21 | SAJ-1 | ATTORNEY LOBBY INTERVIEW INTERCOM DOESN’T WORK. | REWIRED INTERCOM UNIT AND TESTED GOOD.
2009-04-21 | NAJ-3 | SMOKE DETECTOR DIRTY BY ATTORNEY INTERVIEW AREA. | REPLACED DETECTOR AND SYSTEM NORMAL.
2009-04-22 | SAJ-1 | INTERCOMS FOR F & G ARE NOT WORKING. | REPLACED FUSE IN IC28 AMPLIFIER, REPLACED VOLUME CONTROL, AND MIC CABLE SYSTEM NORMAL.
2009-04-22 | SAJ-1 | DOOR CONTROLM SWITCH FOR DORM B IS BROKEN. | REPLACED SWITCH PADDLE.
2009-04-23 | MJ-1 | BOND ROOM #2 PHONE EAR PIECE IS LOOSE AND COMING OFF. | REPLACED PHONE.
2009-04-23 | SAJ-4 | LOUD SPEAL COMING FROM INTERCOM SYSTEM. | CHECKED INTERCOM SYSTEM AND FOUND NOTHING WRONG.
2009-04-25 | MJ-4 | MICROPHONE FOR A,B,C SIDE NOT WORKING. | REPAIRED MICROPHONE. C/O
2009-04-25 | NAJ-3 | MICROPHONE ON A,B,C SIDE NOT WORKING, INMATES CAN’T HEAR. | REPLACED MICROPHONE.C/O
2009-04-26 | SAJ-4 | 9-INCH MONITOR IS OUT LOWER LEFT HAND CORNER. | REPLACED MONITOR.
2009-04-27 | MJ-1 | BOOKING TOGGLE SWITCH FOR OFFICERS ENTRY DOOR BROKEN. | REPLACED TOGGLE. C /O
2009-04-28 | SAJ-2 | TUNNEL INTERCOM SWITCH STAYS ON ALL THE TIME. | REPLACED INTERCOM SWITCH
2009-04-30 | MJ-2 | CENTRAL CONTROL SALLYPORT LAMP FOR INTERCOM IS OUT. | REPLACED LAMP.
2009-04-30 | MJ-1 | BOOKING ENROUTER DOOR WON’T UNLOCK FROM CENTRAL. | REFERRED TO BUILDING ENGINEERS.
2009-04-30 | NAJ-5 | A,B,C SIDE INTERCOM MASTER RESET HARD TO OPERATE. | REPLACED INTERCOM RESET BUTTON.
2009-04-30 | MJ-2 | CENTRAL CONTROL INFIRMARY DOOR TO ELEVATOR #4 UNLOCKS BY ITSELF. | REPLACED TOGGLE SWITCH. C/O
2009-05-01 | SAJ-2 | SMOKE DETECTOR DIRTY MENTAL HEALTH WORK STATION. | CLEANED DETECTOR SYSTEM NORMAL.
2009-05-01 | SAJ-1 | ATTORNEY LOBBY INTERVIEW AREA MINICOM STATION IS DEAD. | RESET SYSTEM OPERATION NORMAL.
2009-05-01 | MJ-2 | CENTRAL CONTROL VEHICLE SALLY PORT DETECTOR DOESN’T WORK. | REPLACED VEHICLE SALLYPORT HOSE.
2009-05-04 | MJ-4 | POD-E INTERCOM VOLUME VERY LOW. | CHECKED INTERCOM OPERATION WITH OFFICER CHECKED GOOD.
2009-05-04 | SAJ-2 | FIRE ALARM SYSTEM WAS DISPLAYING TROUBLE DUE TO ISO CELL #2. | SYSTEM APPEARS NORMAL AT THIS TIME.
2009-05-04 | MJ-2 | CENTRAL CONTROL INNER REAR STAFF DOOR SWITCH NOT OPERATING PROPERLY. | REPLACED DOOR CONTROL SWITCH.
2009-05-05 | SAJ-1 | NO RADIO ON 1ST FLOOR PAGING SYSTEM. | REPLACED 125 WATT AMPLIFIER.
2009-05-08 | MJ-1 | NO RADIO ON 1ST FLOOR. | REPLACED AMPLIFIER.
2009-05-08 | SAJ-2 | ISOLATION CELL #2 ON 1ST FLOOR, INMATE THROWING WATER ON DEVICE. | PUT DEVICE IN DISABLED MODE TO PREVENT RE-OCCURING ALARMS.
2009-05-10 | MJ-BSMT | MINICOMBOX AT BASEMENT SECURITY CAN’T CALL COURT HOLDING. | CHECKED AND FOUND NOTHING WRONG WITH INTERCOM.
2009-05-11 | NAJ-2 | INTERCOM ON D,E,F, SIDE DOESN’T WORK. | REPLACED MASTER RESET SWITCH.
2009-05-13 | NAJ-5 | MINICOM BOX ON D,E, F SIDE DOESN’T ALWAYS WORK. | REPLACED MINCOM BOX.
2009-05-13 | SAJ-1 | SECURITY STATION 1ST FLOOR CUE UP MONITOR SHOWS A DARK PICTURE. | REPLACED MONITOR.
2009-05-13 | SAJ-1 | CAMERA IN F & G HALLWAY SHOWS TOO DARK VIDEO. | REPLACED CAMERA.
2009-05-13 | MJ-4 | FIRA ALRM TAMPER SWITCH FAILED AND WAS REPLACED BY JERICO. | WIRED DEVICE AND CHECKED OPERATION.
2009-05-13 | SAJ-2 | PLUNBING CHASE DOOR BETWEEN F & G SHOWS RED. | SOFTWARE FOR ALARM TAKES LONG TO RESET.
2009-05-15 | MJ-6 | 6F-15 SHOWS RED WHEN SECURE. | NEED LOCKSMITH TO CHECK LOCK STATUS SWITCH.
2009-05-15 | SAJ-4 | MICROPHONE NOT WORKING IN SECURITY STATION. | REPAIRED BROKEN CORD GOING TO MICROPHONE.
2009-05-15 | MJ-4 | 4TH FLOOR TAMPER SWITCH INSTALLED. | RE-WIRED TAMPER SWITCH.
2009-05-18 | SAJ-1 | ISOLATION CELL #1 INMATE CAN’T BE HEARD OVER INTERCOM. | REPAIRED WIRING ON THE BACK OF RELAY PANEL.
2009-05-18 | MJ-1 | FIRE ALARM ACTIVATED. | PANEL WAS RESET BEFORE COULD DETERMINE DEVICE IN ALARM.
2009-05-21 | SAJ-4 | MINICOM BOX CORD IS DAMAGED. | REPLACED CORD.
2009-05-22 | MJ-5 | 5FF1 HAS A BROKEN TOGGLE SWITCH. | REPLACED TOGGLE.
2009-05-25 | SAJ-1 | ATTORNEY LOBBY SECURITY FRONT DOOR CONTROL BOX HAS BAD SWITCHES. | REPLACED 2 SWITCHES AND REPLACED FUSE. C/O
2009-05-25 | MJ-3 | POD-C CELL CHASE BETWEEN 7& 8 WATER LEAK DETECTOR WON’T RESET. | REMOVED DETECTOR AND INSTALLED BYPASS UNTIL WATER LEAK IS FIXED.
2009-05-26 | MJ-4 | CELL 4FF1 DOESN’T LIGHT UP IN SECURITY STATION. | REPAIRED CELL INTERCOM SWITCH.
2009-05-27 | MJ-6 | CELL 6D-3 WON’T UNLOCK FROM SECURITY OR WITH KEY. | DOOR BINDING ON LOCK, REFERRED TO ENGNEER.
2009-05-28 | NAJ-1 | WELDING IN DORM D ON INMATE STAIR RAILING. | BYPASSED FIRE ALARM SYSTEM AND RE-ENABLED. SYSTEM NORMAL.
2009-05-28 | SAJ-1 | WELDING IN DORM-A . | BYPASSED FIRE ALARM SYSTEM AND RE-ENABLED. SYSTEM NORMAL.
2009-06-04 | SAJ-3 | CHECK MICROPHONE NOT ALWAYS TRANSMITTING. | REPLACED MICROPHONE.
2009-06-04 | MJ-2 | PNEUMATIC TUBE SYSTEM IN MAIN JAIL HAS WEAK VACUM. | REPLACED 1 VACUM MOTOR.
2009-06-08 | MJ-6 | MICROPHONE ON D,E,F SIDE NOT WORKING. | REPLACED MICROPHONE.
2009-06-08 | SAJ-1 | INTERCOM IN ATTORNEY LOBBY NOT WORKING. | REPLACED INTERCOM STATION AND REPAIRED WIRING.
2009-06-08 | MJ-BSMT | ELEVATOR #2 DOOR SHOWS RED WHEN SECURE. | REFERRED PROBLEM TO LOCKSMITH.
2009-06-08 | MJ-5 | CAMERA THAT LOOKS AT FRONT OF SECURITY STATION DOOR LOOKS DOWN. | FOUND NOTHING WRONG. SOFTWARE ON HISTORY PLAYBACK ZOOMED IN.
2009-06-09 | MJ-1 | BOND ROOM #1 VISITORS SIDE PHONE IS DAMAGED. | REPLACED PHONE.
2009-06-09 | NAJ-1 | CENTRAL CONTROL ELEVATOR #1 MONITOR IS OUT. | REPLACED MONITOR.
2009-06-09 | MJ-2 | CENTRAL CONTROL INFIRMARY DOOR HAS BROKEN SWITCH. | REPLACED SWITCH PADDLE.
2009-06-11 | MJ-2 | CENTRAL CONTROL INFIRMARY DOOR DOESN’T SHOW SOLID RED. | REPLACED DOOR CONTROL SWITCH.
2009-06-15 | MJ-6 | SECURITY ELEVATOR #3 DOOR UNLOCKS DOOR BY ITSELF. | REPLACED DOOR CONTROL SWITCH.
2009-06-15 | MJ-5 | MICROPHONE ON A SIDE IS INTERMITTEN. | CHECKED MICROPHONE AND FOUND NOTHING WRONG.
2009-06-15 | SAJ-1 | CAMERA CALL-UP SWITCHES LIGHTS ARE OUT. | RELAMPED CALL UP SWITCHES.
2009-06-15 | MJ-6 | MINI COM BOX ON B SIDE NOT WORKING. | CHECKED OK.
2009-06-16 | SAJ-2 | 2D-SHOWER-INTERCOM-ACTIVATES INTERMITTENLY. | REPLACED INTERCOM SWITCH.
2009-06-16 | NAJ-CC | BUTTONS FOR INNER AND OUTER VESTIBULE-DOORS-ARE-HARD-TO ACTIVATE. | REPLACED BUTTONS.
2009-06-16 | NAJ-2 | MASTER UNLOCK BUTTONS HARD TO ACTIVATE. | REPLACED SWITCHES WITH SURFACE MOUNTED.
2009-06-18 | SAJ-3 | DORM 3-D INTERCOM SQUEALS AT TIMES. | SYSEM RESET ALL NORMAL.
2009-06-19 | SAJ-2 | SECURITY STATION MONITOR FOR QUAD IS OUT. | REPLACED MONITOR.
2009-06-22 | NAJ-1 | EAST STAIR CAMERA #114 VIDEO KEEPS TRIPING MOTION ALARM. | REPLACED CAMERA.
2009-06-22 | MJ-6 | STATION #1 IS DOWN. | LOADER ARM NEEDED TO BE REFASTENED.
2009-06-22 | MJ-2 | ELEVATOR #2 HAS BAD VIDEO. | REPLACED FITTING FOR CAMERA ABOVE ELEV CAR.
2009-06-23 | NAJ-3 | VIDEO SWITCHER FOR B SIDE HAS PROBLEMS. | REMOVED UNIT SENT INTO PELCO FOR REPAIR.
2009-06-29 | MJ-3 | ELEVATOR #2 VESTIBULE SWITCH IS BROKEN. | REPLACED SWITCH PADDLE.
2009-06-29 | SAJ-1 | SECURITY STATION DORM ENTRY SWITCH IS BROKEN. | REPLACED SWITCH.
2009-06-29 | NAJ-4 | A-SIDE SECURITY STATION MICROPHONE IS INTERMITTEN. | REPLACED MICROPHONE.
2009-06-29 | NAJ-4 | A-SIDE SECURITY STATION INTERCOM IS INTERMITTEN. | REPLAQCED VOLUME DOWN CONTROL SWITCH.
2009-06-30 | NAJ-4 | A-SIDE INTERCOM SYSTEM NOT WORKING, CUTS IN AND OUT. | REPLACED AMPLIFIER FOR A-SIDE.
2009-06-30 | MJ-3 | GROUP UNLOCK SWITCH UNLOCKS 3B13 WHEN IN PRORITY POSITION. | REPLACED DOOR INTERFACE BOARD.
2009-06-30 | NAJ-1 | CENTRAL CONTROL RADIO VOLUME CONTROL NOT WORKING. | REPLACED CONSOLE VOLUME CONTROL.